## S-1793
Name of the work: Erection of new 33/11kV P&T Colony Outdoor sub-Station with connected 33kV and 11kV Lines at P&T Colony in Himayathsagar (M), Rajendranagar Circle in ECGH Division/Master plan/RR Circle- under Improvement works
WBS N0:S-1793-13-03-02-01-001
S.No | QTY | Item Detailed Specification Description | Work Type | Item short Description | APSS/MorthCI Number() | Rate(INR) | UOM | Amount
1 | 16 | Loading of R.S. Joists 150 x 150mm / Rail poles | elect | Labour | SWR10205 | 176 | EA | 2816
2 | 5.76 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | elect | Labour | SWR10132 | 412.08 | TO | 2373.5808
3 | 16 | Un loading of R.S. Joists 150 x 150mm / Rail poles | elect | Labour | SWR10523 | 107 | EA | 1712
4 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | elect | Labour | SWR11039 | 928 | EA | 14848
| 5.76 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | elect | labour | SWR10868 | 6852 | TO | 39467.52
5 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | elect | supply | SMR40009 | 2181 | TO | 12562.56
6 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | elect | labour | SWR10877 | 851 | TO | 4901.76
7 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | elect | supply | SMR40010 | 1293 | TO | 7447.68
8 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | elect | labour | SWR10879 | 482 | TO | 2776.32
| 5.76 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | elect | labour | swr10867 | 1470 | TO | 8467.2
9 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | elect | labour | SWR10348 | 1952.61 | EA | 31241.76
10 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | elect | labour | SWR10356 | 6579 | M3 | 116829.882
11 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | elect | labour | SWR10862 | 373 | M2 | 3446.52
12 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | elect | labour | SWR11089 | 48 | EA | 768
13 | 4 | Loading of R.S. Joists 175 x 85 mm | elect | labour | SWR10204 | 76 | EA | 304
14 | 1 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | elect | Labour | SWR10132 | 412.08 | TO | 412.08
15 | 4 | Un loading of R.S. Joists 175 x 85 mm | elect | labour | SWR10522 | 50 | EA | 200
16 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | elect | labour | SWR11037 | 793 | EA | 3172
18 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | elect | supply | SMR40009 | 2181 | TO | 2181
19 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | elect | labour | SWR10877 | 851 | TO | 851
20 | 1 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | elect | supply | SMR40010 | 1293 | TO | 1293
21 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | elect | labour | SWR10879 | 482 | TO | 482
22 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | elect | labour | SWR20863 | 1044.23 | EA | 4176.92
23 | 2.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | elect | labour | SWR10356 | 6579 | M3 | 17434.35
24 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | elect | labour | SWR10862 | 373 | M2 | 861.63
25 | 4 | Paint of coping with 2 coats of white cement incl cost of paints etc. | elect | labour | SWR11089 | 48 | EA | 192
26 | 5.063 | Loading of M.S.Channels, Angles, Flats & Rods etc., | elect | labour | SWR10206 | 221 | TO | 1118.923
27 | 5.063 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | elect | Labour | SWR10132 | 412.08 | TO | 2086.361
28 | 5.063 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | elect | labour | SWR10524 | 185 | TO | 936.655
29 | 5.063 | Fabrication & erection of Channels-Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | elect | Labour | SWR10868 | 6852 | TO | 34691.676
30 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | elect | supply | SMR40009 | 2181 | TO | 11042.403
31 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | elect | labour | SWR10877 | 851 | TO | 4308.613
32 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | elect | supply | SMR40010 | 1293 | TO | 6546.459
33 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | elect | labour | SWR10879 | 482 | TO | 2440.366
34 | 5.063 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | elect | labour | SWR10867 | 1470 | TO | 7442.61
35 | 13 | Loading of 33KV 800 Amps AB Switch | elect | labour | SWR10239 | 126 | EA | 1638
36 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | elect | labour | SWR11861 | 3299.7 | EA | 6599.4
37 | 13 | Un loading of 33KV 800 Amps AB Switch | elect | labour | SWR10557 | 79 | EA | 1027
38 | 13 | Erection of 33 KV AB Switch including alignment and earthing | elect | labour | SWR10392 | 4500 | EA | 58500
39 | 34 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | elect | labour | SWR10881 | 142 | EA | 4828
40 | 34 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | elect | labour | SWR12331 | 146.63 | EA | 4985.42
41 | 6 | Loading of 33 KV CTs/ PTs | elect | labour | SWR10200 | 165 | EA | 990
42 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | elect | labour | SWR11861 | 3299.7 | EA | 3299.7
43 | 6 | Un loading of 33 KV CTs/ PTs | elect | labour | SWR10518 | 128 | EA | 768
44 | 2 | Erection of 33kv single phase PT s | elect | labour | SWR10401 | 1079 | SET | 2158
45 | 12 | Loading of 33 KV, 10 KA LAs Station typ | elect | labour | SWR10266 | 41 | EA | 492
46 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | elect | labour | SWR11861 | 3299.7 | EA | 3299.7
47 | 12 | Un loading of 33 KV, 10 KA LAs Station type | elect | labour | SWR10584 | 35 | EA | 420
48 | 4 | Erection of 33 KV LAS station/Line type including earthing | elect | labour | SWR10396 | 880 | SET | 3520
49 | 2 | Loading of 33 KV VCBs along with Panel boards | elect | labour | SWR10198 | 1024 | EA | 2048
50 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | elect | labour | SWR11861 | 3299.7 | EA | 3299.7
51 | 2 | Un loading of 33 KV VCBs along with Panel boards | elect | labour | SWR10516 | 1044.48 | EA | 2088.96
52 | 12.584 | Excavate-Pit for 33KV VCB | elect | labour | SWR23224 | 331 | M3 | 4165.304
53 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | elect | labour | SWR20685 | 5160 | M3 | 74923.2
54 | 2 | Erection of 33 KV VCB with Control Panel | elect | labour | SWR10460 | 12500 | EA | 25000
55 | 2 | Loading and unloading of PTR on constructed plinth-Loading of 8MVA PTR | elect | labour | SWR10613 | 5805.84 | EA | 11611.68
56 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | elect | labour | SWR10854 | 21945 | EA | 43890
57 | 2 | unloading of 8 MVA PTR | elect | labour | SWR10627 | 5805.84 | EA | 11611.68
58 | 700 | S/o rail poles 90/105lb (250x2N) | elect | supply | SMR22718 | 47.27 | KG | 33089
59 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | elect | labour | SWR10344 | 3510 | EA | 49140
60 | 2 | Erection of 8 MVA PTR | elect | labour | SWR21321 | 49480.2 | EA | 98960.4
61 | 0.436 | Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | elect | supply | SMR24910 | 299369 | KM | 130524.884
62 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | elect | supply | SMR11915 | 2055 | SET | 61650
63 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | elect | supply | SMR22473 | 294 | EA | 8820
64 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . | elect | supply | SMR40011 | 299 | EA | 13455
65 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) | elect | labour | SWR21240 | 781 | EA | 4686
66 | 84 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | elect | labour | SWR10404 | 327.68 | M | 27525.12
67 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | elect | labour | SWR10884 | 224 | EA | 6720
68 | 75 | Labour for Fixing of all types of clamps | elect | labour | SWR10917 | 65 | EA | 4875
69 | 25 | Loading of R.S. Joists 150 x 150mm / Rail poles | elect | Labour | SWR10205 | 176 | EA | 4400
70 | 8.68 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | elect | Labour | SWR10132 | 412.08 | TO | 3576.8544
71 | 25 | Un loading of R.S. Joists 150 x 150mm / Rail poles | elect | Labour | SWR10523 | 107 | EA | 2675
72 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | elect | Labour | SWR11039 | 928 | EA | 23200
73 | 8.68 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | elect | Labour | SWR10868 | 6852 | TO | 59475.36
74 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc.Sup Material for 1st coat Al. Painting. | elect | supply | SMR40009 | 2181 | TO | 18931.08
75 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | elect | labour | SWR10877 | 851 | TO | 7386.68
76 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | elect | supply | SMR40010 | 1293 | TO | 11223.24
77 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | elect | labour | SWR10879 | 482 | TO | 4183.76
78 | 8.68 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | elect | labour | SWR10867 | 1470 | TO | 12759.6
79 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly amming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | elect | labour | SWR10348 | 1952.61 | EA | 48815.25
80 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | elect | labour | SWR10356 | 6579 | M3 | 182567.25
81 | 17.91 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | elect | labour | SWR10862 | 373 | M2 | 6680.43
82 | 25 | Paint of coping with 2 coats of white cement incl cost of paints etc. | elect | labour | SWR11089 | 48 | EA | 1200
83 | 4.642 | Loading of M.S.Channels, Angles, Flats & Rods etc., | elect | labour | SWR10206 | 221 | TO | 1025.882
84 | 4.642 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | elect | Labour | SWR10132 | 412.08 | TO | 1912.8754
85 | 4.642 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | elect | labour | SWR10524 | 185 | TO | 858.77
86 | 4.642 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | elect | Labour | SWR10868 | 6852 | TO | 31806.984
87 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | elect | supply | SMR40009 | 2181 | TO | 10124.202
88 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | elect | labour | SWR10877 | 851 | TO | 3950.342
89 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | elect | supply | SMR40010 | 1293 | TO | 6002.106
90 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | elect | labour | SWR10879 | 482 | TO | 2237.444
91 | 4.642 | Fabrication & erection of Channels-Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | elect | labour | SWR10867 | 1470 | TO | 6823.74
92 | 20 | Loading of 11KV AB Switch Conventional type | elect | labour | SWR10238 | 80 | EA | 1600
93 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | elect | labour | SWR11861 | 3299.7 | EA | 6599.4
94 | 20 | Un loading of 11KV AB Switch Conventional type | elect | labour | SWR10556 | 80 | EA | 1600
95 | 17 | Erection of 11KV 800A double throw AB Switches and aligment complete | elect | labour | SWR21277 | 3500 | EA | 59500
96 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | elect | labour | SWR10393 | 3200 | EA | 9600
97 | 2 | Loading of 11 KV CT - PT Sets | elect | labour | SWR10201 | 190 | EA | 380
98 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | elect | labour | SWR11861 | 3299.7 | EA | 3299.7
99 | 2 | Un loading of 11 KV CT - PT Sets | elect | labour | SWR10519 | 101 | EA | 202
100 | 2 | Erection of 11 KV three phase PTs | elect | labour | SWR10402 | 800 | SET | 1600
101 | 24 | Loading of 11 KV, 10 KA LAs Station type | elect | labour | SWR10264 | 32 | EA | 768
102 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | elect | labour | SWR11861 | 3299.7 | EA | 3299.7
103 | 24 | Un loading of 11 KV, 10 KA LAs Station type | elect | labour | SWR10582 | 32 | EA | 768
104 | 2 | Erection of 11 KV LAS station type including earthing | elect | labour | SWR10397 | 559 | SET | 1118
105 | 6 | Erection of 11 KV LAS line type including earthing | elect | labour | SWR10398 | 505 | SET | 3030
106 | 8 | Loading of 11 KV VCBs along with Panel boards | elect | labour | SWR10199 | 1024 | EA | 8192
107 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | elect | labour | SWR11861 | 3299.7 | EA | 13198.8
108 | 8 | Un Loading of 11 KV VCBs along with Panel boards | elect | labour | SWR10517 | 1044.48 | EA | 8355.84
109 | 41.6 | Excavate-Pit for 33KV VCB | elect | labour | SWR23224 | 331 | M3 | 13769.6
110 | 48 | Cement concrete 1:3:6 ration with 40 MML HBG metalincluding the cost of all materials and labour complete 1.8 x1.8 x 0.75 cum for VCB Plinth | elect | labour | SWR20685 | 5160 | M3 | 247680
111 | 8 | Erection of 11 KV VCB with Control Panel | elect | labour | SWR10461 | 12000 | EA | 96000
112 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | elect | supply | SMR11915 | 2055 | SET | 24660
113 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | elect | supply | SMR22473 | 294 | EA | 3528
114 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | elect | supply | SMR40011 | 299 | EA | 13455
115 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | elect | labour | SWR21241 | 507 | EA | 1014
116 | 63 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | elect | labour | SWR10404 | 327.68 | M | 20643.84
117 | 45 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | elect | labour | SWR10884 | 224 | EA | 10080
118 | 57 | Labour for Fixing of all types of clamps | elect | labour | SWR10917 | 65 | EA | 3705
119 | 4 | Loading of M.S.Channels, Angles, Flats & Rods etc., | elect | labour | SWR10206 | 221 | TO | 884
120 | 4 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | elect | Labour | SWR10132 | 412.08 | TO | 1648.32
121 | 4 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | elect | labour | SWR10524 | 185 | TO | 740
122 | 584 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. | elect | labour | SWR10920 | 65 | RMT | 37960
123 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | elect | labour | SWR10919 | 41 | RMT | 41410
124 | 36 | Supply of earthing pipe with materials -Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | elect | supply | SMR11482 | 3486 | EA | 125496
125 | 36 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | elect | labour | SWR10357 | 1234.2 | EA | 44431.2
126 | 36 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | elect | labour | SWR10359 | 386 | EA | 13896
127 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. | elect | supply | SMR40033 | 4725 | EA | 9450
128 | 2 | Providing of earthing with various types of earth electrodes-Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | elect | labour | SWR11892 | 1323 | EA | 2646
129 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | elect | labour | SWR11702 | 200 | DR | 800
130 | 80 | Providing of control cable trench as per DATA-XII | elect | labour | SWR22093 | 3148 | RMT | 251840
131 | 3074 | Control Cable-Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | elect | labour | SWR11879 | 27 | M | 82998
132 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | elect | labour | SWR12510 | 27 | EA | 7290
133 | 4 | Supply of FRP PT Marshalling Box | elect | supply | SMR40048 | 4463 | EA | 17852
134 | 4 | Erection of Marshalling boxes | elect | labour | SWR10940 | 374.85 | EA | 1499.4
135 | 1 | Loading of 220 V Batterry with charger | elect | labour | SWR11166 | 1612 | SET | 1612
136 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | elect | labour | SWR11861 | 3299.7 | EA | 3299.7
137 | 1 | Un loading of 220 V Batterry with charger | elect | labour | SWR11147 | 1024 | SET | 1024
138 | 1 | Erection of 220 V, 200 AH battery in complete shape fit for charging . Conventional lead acid | elect | labour | SWR12350 | 7666 | EA | 7666
139 | 1 | Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | elect | supply | SMR40044 | 42500 | EA | 42500
140 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | elect | supply | SMR40045 | 42000 | EA | 42000
141 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | elect | labour | SWR20025 | 7871.85 | SET | 15743.7
142 | 8 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | elect | supply | SMR40051 | 13913 | EA | 111304
143 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | elect | supply | SMR11594 | 8200 | EA | 65600
144 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | elect | Labour | SWR11039 | 928 | EA | 7424
145 | 8 | Erection of tubular poles | elect | labour | SWR10955 | 1379 | EA | 11032
146 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | elect | labour | SWR10356 | 6579 | M3 | 34671.33
147 | 8 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete | elect | labour | SWR10956 | 1268 | EA | 10144
148 | 45 | Supply of HBG metal-Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | elect | labour | SWR10860 | 2113 | M3 | 95085
149 | 3 | Loading of R.S. Joists 175 x 85 mm | elect | labour | SWR10204 | 76 | EA | 228
150 | 0.75 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | elect | Labour | SWR10132 | 412.08 | TO | 309.06
151 | 3 | Un loading of R.S. Joists 175 x 85 mm | elect | labour | SWR10522 | 50 | EA | 150
152 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | elect | labour | SWR11040 | 990.68 | EA | 1981.36
153 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | elect | supply | SMR40009 | 2181 | TO | 1635.75
154 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | elect | labour | SWR10877 | 851 | TO | 638.25
155 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | elect | supply | SMR40010 | 1293 | TO | 969.75
156 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | elect | labour | SWR10879 | 482 | TO | 361.5
157 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | elect | labour | SWR11267 | 3901.37 | EA | 3901.37
158 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | elect | labour | SWR10356 | 6579 | M3 | 14605.38
159 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | elect | labour | SWR10862 | 373 | M2 | 432.68
160 | 2 | Paint of coping with 2 coats of white cement incl cost of paints etc. | elect | labour | SWR11089 | 48 | EA | 96
161 | 1 | Construction of DTR Plinth-RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | elect | labour | SWR21843 | 25967.57 | EA | 25967.57
162 | 1 | Loading of 50,63, 75 & 100 KVA DTR | elect | labour | SWR10195 | 350 | EA | 350
163 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | elect | labour | SWR11861 | 3299.7 | EA | 3299.7
164 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | elect | labour | SWR10513 | 280 | EA | 280
165 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Phase DTRs 63,75 & 100 KVA | elect | labour | SWR20905 | 1650 | EA | 1650
166 | 1 | Loading of 11 KV AB SWCH T.T.200/400 A | elect | labour | SWR12406 | 80 | EA | 80
167 | 1 | Un loading of 11 KV AB SWCH T.T.200/400 A | elect | labour | SWR12425 | 80 | EA | 80
168 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | elect | labour | SWR20102 | 1813.49 | EA | 1813.49
169 | 1 | Loading of 11 KV HG Fuse Sets | elect | labour | SWR10231 | 18 | EA | 18
170 | 1 | Un loading of 11 KV HG Fuse Sets Set ₹ | elect | labour | SWR10549 | 18 | EA | 18
171 | 1 | Erect. of 11kv HG Fuseset incl earthing | elect | labour | SWR10395 | 740.52 | SET | 740.52
172 | 40 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | elect | labour | SWR11920 | 465.46 | M | 18618.4
173 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | elect | labour | SWR11956 | 126.23 | M | 2524.6
174 | 2 | Making of Outdoor/Indoor End Termination Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | elect | labour | SWR10390 | 2370.63 | EA | 4741.26
175 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | elect | labour | SWR10674 | 1594.67 | EA | 1594.67
176 | 85 | LAYING OF 33KV, 11KV UG CABLE Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | elect | labour | SWR11923 | 377.63 | M | 32098.55
177 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | elect | labour | SWR11959 | 85.43 | M | 1281.45
178 | 2 | UG Cables Joints :-Making of Outdoor/Indoor End Termination -Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x185 Sqmm Cable | elect | labour | SWR10765 | 968.9 | EA | 1937.8
179 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | elect | labour | SWR20032 | 1654 | EA | 1654
180 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. | elect | labour | SWR22090 | 2205 | EA | 2205
181 | 750 | Supplying & fabrication erection of 6mm Checkerd plates asper the field conditions | elect | labour | SWR10873 | 83 | KG | 62250
182 | 1 | T & P Supply of Wall clock standard make | elect | supply | SMR40059 | 578 | EA | 578
183 | 1 | S-10ft Aluminium Ladder | elect | supply | SMR12378 | 1654 | EA | 1654
184 | 1 | Sup Alluminium Ladder for indoor works | elect | supply | SMR40062 | 4410 | EA | 4410
185 | 30 | T & P Painting of Name Plates for any equipmen | elect | labour | SWR10963 | 122 | EA | 3660
186 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7,8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | elect | supply | SMR40063 | 4925 | SET | 4925
187 | 1 | T & P Sup Rechargeable LED torch light of Standard make | elect | supply | SMR40064 | 1733 | EA | 1733
188 | 1 | T & P-Steel almarah(61/2 X 3ft) Godrej | elect | supply | SMR40061 | 9818 | EA | 9818
189 | 1 | T & P-Table (3x6ft) Godrej | elect | supply | SMR40057 | 6050 | EA | 6050
190 | 4 | T & P-S type chairs (Godrej) | elect | supply | SMR40058 | 924 | EA | 3696
191 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | elect | supply | SMR40060 | 1733 | EA | 1733
192 | 1 | T & P Supply of Hack saw (12 inches) | elect | supply | SMR40065 | 289 | EA | 289
193 | 4 | Sup Earth Rods (8ft) Screw & clamp type | elect | supply | SMR40066 | 578 | EA | 2312
194 | 2 | Supply of Hand Gloves | elect | supply | SMR40067 | 289 | SET | 578
195 | 12 | SupRubber mats( 6'x3')size fo indoorSS | elect | supply | SMR40068 | 1386 | EA | 16632
196 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | elect | supply | SMR40069 | 1386 | EA | 1386
197 | 14 | Supply of Danger boards with clamps | elect | supply | SMR40070 | 116 | EA | 1624
198 | 2 | Fire bucket stand with 3 buckets (8 -10 ltr capacity) | elect | supply | SMR40088 | 1386 | SET | 2772
199 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | elect | supply | SMR40089 | 4620 | EA | 9240
200 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | elect | supply | SMR40087 | 9240 | EA | 36960
201 | 6 | Supply of Safety Helmet of standard make | elect | supply | SMR40071 | 231 | EA | 1386
202 | 8 | Supply of LC Boards | elect | supply | SMR40072 | 116 | EA | 928
203 | 4 | Supply of Gum Boots(Pairs) | elect | supply | SMR40073 | 693 | EA | 2772
204 | 1 | Supply of 5000v megger | elect | supply | SMR40074 | 13860 | EA | 13860
205 | 1 | Supply of Earth megger (1000v) | elect | supply | SMR40075 | 8085 | EA | 8085
206 | 1 | Supply of Digital clamp meter. | elect | supply | SMR40076 | 2888 | EA | 2888
207 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | elect | supply | SMR40086 | 10238 | EA | 10238
208 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | elect | supply | SMR12488 | 90 | KG | 72000
209 | 2 | Fabrication of poles-Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | elect | labour | SWR10642 | 512.55 | EA | 1025.1
210 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | elect | labour | SWR10346 | 1934 | EA | 1934
211 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm | elect | labour | SWR11713 | 204 | DR | 816
212 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | elect | labour | SWR11861 | 3299.7 | EA | 6599.4
213 | 7 | survey line&cabl inc peg mark&tree clear | elect | labour | SWR22092 | 765 | KM | 5355
214 | 7 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Single Circuit (3 Conductors) | elect | labour | SWR10366 | 13856.7 | KM | 96996.9
215 | 120 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | elect | labour | SWR11040 | 990.68 | EA | 118881.6
216 | 120 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | elect | labour | SWR10978 | 4336.85 | EA | 520422
217 | 36.855 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | elect | labour | SWR10356 | 6579 | M3 | 242469.045
218 | 120 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)-11 Mtrs long PSCC Poles | elect | labour | SWR11180 | 431.97 | EA | 51836.4
219 | 120 | Painting of poles-Numbering of poles incl. cost of paint | elect | labour | SWR10378 | 32 | EA | 3840
220 | 30 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | elect | labour | SWR10107 | 700 | EA | 21000
221 | 30 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erec of 9.1 Mts PSCC poles for stuts | elect | labour | SWR11083 | 2400 | EA | 72000
222 | 12.15 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | elect | labour | SWR10356 | 6579 | M3 | 79934.85
223 | 30 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)-9.1 Mtrs long PSCC Poles | elect | labour | SWR20308 | 407.29 | EA | 12218.7
224 | 20 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | elect | labour | SWR10653 | 1435.81 | EA | 28716.2
225 | 200 | S-GI Bolts & Nuts,Washers etc., | elect | supply | SMR11488 | 117.5 | KG | 23500
226 | 7 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | elect | labour | SWR11861 | 3299.7 | EA | 23097.9
227 | 7 | LOADING of Conductor drums | elect | labour | SWR10191 | 202 | EA | 1414
228 | 7 | UNLOADING of Conductor drums | elect | labour | SWR10509 | 100 | EA | 700
229 | 100 | Loading of 33 KV Pin insulators | elect | labour | SWR10211 | 3 | CRT | 300
230 | 100 | Un loading of 33 KV Pin insulators | elect | labour | SWR10529 | 3 | CRT | 300
231 | 15 | Loading of 33 KV Metal parts | elect | labour | SWR10618 | 65 | BAG | 975
232 | 15 | Un loading of 33 KV Metal parts | elect | labour | SWR10632 | 65 | BAG | 975
233 | 460 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | elect | labour | SWR11980 | 1388.84 | M | 638866.4
234 | 460 | Laying of 2nd cable in excavated trench | elect | labour | SWR10988 | 204.1 | M | 93886
235 | 40 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | elect | labour | SWR12004 | 323.85 | M | 12954
236 | 12 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | elect | supply | SMR40081 | 1044 | M | 12528
237 | 30 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | elect | supply | SMR40077 | 363 | M | 10890
238 | 5 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | elect | supply | SMR40085 | 484 | EA | 2420
239 | 8 | Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination 33kv 3x400 xlpe | elect | labour | SWR10387 | 2764.76 | EA | 22118.08
240 | 2 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | elect | labour | SWR10382 | 5700.78 | EA | 11401.56
241 | 2 | Loading of 33/KV XLPE UG CableStraight Through Joint Kits for all sizes | elect | labour | SWR11172 | 8 | EA | 16
242 | 2 | Un loading of 33/KV XLPE UG CableStraight Through Joint Kits for all sizes | elect | labour | SWR11153 | 4 | EA | 8
243 | 2.7 | Fabrication & erection of Channels -Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | elect | labour | SWR10869 | 3426 | TO | 9250.2
244 | 50 | Supply of earthing pipe with materials-Supply of GI wire No 8 | elect | supply | SMR11486 | 105 | KG | 5250
245 | 2 | Supply of earthing pipe with materials-Supply of CI eath pipe with 80mm dia,2.0 M Length | elect | supply | SMR11483 | 2789 | EA | 5578
246 | 2 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | elect | labour | SWR10357 | 1234.2 | EA | 2468.4
247 | 2 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | elect | labour | SWR10359 | 386 | EA | 772
248 | 40 | Supply of earthing pipe with materials-Supply of GI Flat 25X3 mm | elect | supply | SMR11485 | 105 | KG | 4200
249 | 20 | Supply of Danger boards with clamps | elect | supply | SMR40070 | 116 | EA | 2320
250 | 5 | S&E-Smart RFID marker | elect | labour | SWR25089 | 2745 | EA | 13725
251 | 2.7 | Loading of M.S.Channels, Angles, Flats & Rods etc., | elect | labour | SWR10206 | 221 | TO | 596.7
252 | 2.7 | Un loading of CT Metering/Distribution boxes with meters | elect | labour | SWR10542 | 18 | EA | 48.6
253 | 2.7 | Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading)-Above 50 KM and upto 80 KM | elect | labour. | SWR10151 | 718.08 | TO | 1938.816
254 | 4 | Load-11/33KV XLPE UG Cable for all sizes | elect | labour | SWR11230 | 1024 | DR | 4096
255 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | elect | labour | SWR11861 | 3299.7 | EA | 6599.4
256 | 4 | Unload-11/33KV XLPE UG Cable for all sizes | elect | labour | SWR11231 | 1024 | DR | 4096
257 | 9 | survey line&cabl inc peg mark&tree clear | elect | labour | SWR22092 | 765 | KM | 6885
258 | 9 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-55 Sqmm Single Circuit (3 Conductors) | elect | labour | SWR10365 | 9454.81 | KM | 85093.29
259 | 175 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | elect | labour | SWR10107 | 700 | EA | 122500
260 | 50 | Excavation of pits in hard rock requiring blasting. (other than SS)-9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | elect | labour | SWR10112 | 1770 | EA | 88500
261 | 213 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-9.1 M long PSCC pole | elect | labour | SWR10343 | 2400 | EA | 511200
262 | 33.29 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | elect | labour | SWR10356 | 6579 | M3 | 219014.91
263 | 225 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)-9.1 Mtrs long PSCC Poles | elect | labour | SWR20308 | 407.29 | EA | 91640.25
264 | 225 | Painting of poles-Numbering of poles incl. cost of paint | elect | labour | SWR10378 | 32 | EA | 7200
265 | 80 | Excavation of pits in all soils except hard rock requiring blasting-Stud Poles 0.6 M x 0.9 M x 1.5 M | elect | labour | SWR10106 | 645 | EA | 51600
266 | 80 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-8.0 m long PSCC poles for Strut | elect | labour | SWR21590 | 1500 | EA | 120000
267 | 32.4 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | elect | labour | SWR10356 | 6579 | M3 | 213159.6
268 | 80 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)-8 Mtrs long PSCC Poles | elect | labour | SWR20307 | 271.52 | EA | 21721.6
269 | 40 | Formation of Cut points - Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | elect | labour | SWR10653 | 1435.81 | EA | 57432.4
270 | 350 | S-GI Bolts & Nuts,Washers etc., | elect | supply | SMR11488 | 117.5 | KG | 41125
271 | 9 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | elect | labour | SWR11861 | 3299.7 | EA | 29697.3
272 | 9 | LOADING of Conductor drums | elect | labour | SWR10191 | 202 | EA | 1818
273 | 9 | UNLOADING of Conductor drums | elect | labour | SWR10509 | 100 | EA | 900
274 | 6 | Supply of earthing pipe with materials-Supply of CI eath pipe with 50mm dia,2.0 M Length | elect | supply | SMR11484 | 2441 | EA | 14646
275 | 6 | Providing of Earthing-Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | elect | labour | SWR10357 | 1234.2 | EA | 7405.2
276 | 6 | Providing of RCC collar to earth pit-Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | elect | labour | SWR10359 | 386 | EA | 2316
277 | 6 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting.-11KV DP Structure with 9.1 Mtrs PSCC Poles | elect | labour | SWR21130 | 3363.96 | SET | 20183.76
278 | 6 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | elect | labour | SWR10393 | 3200 | EA | 19200
279 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | elect | labour | SWR10881 | 142 | EA | 852
280 | 200 | Supply of earthing pipe with materials-Supply of GI wire No 8 | elect | supply | SMR11486 | 105 | KG | 21000
281 | 675 | Loading of 11KV Polymer Pin Insulators with GI pins | elect | labour | SWR11248 | 1 | EA | 675
282 | 675 | Un loading of 11KV Polymer Pin Insulators with GI pins | elect | labour | SWR11249 | 1 | EA | 675
283 | 240 | Loading of 11KV Polymer Pin Insulators with GI pins | elect | labour | SWR11248 | 1 | EA | 240
284 | 240 | Un loading of 11KV Polymer Pin Insulators with GI pins | elect | labour | SWR11249 | 1 | EA | 240
285 | 6 | Loading of 11 KV Metal parts | elect | labour | SWR12402 | 48 | BAG | 288
286 | 6 | Un loading of 11 KV Metal parts | elect | labour | SWR12421 | 48 | BAG | 288
287 | 960 | Excavation & laying of UG Cable (Double Run)-Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC-11 KV 3x300 Sqmm Cable | elect | labour | SWR11973 | 631.06 | M | 605817.6
288 | 960 | Laying of 2nd cable in excavated trench | elect | labour | SWR10988 | 204.1 | M | 195936
289 | 240 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x300 Sqmm Cable | elect | labour | SWR12005 | 275.4 | M | 66096
290 | 72 | Cost of Pipes and slabs-Supply of 6" B class GI pipe | elect | supply | SMR40081 | 1044 | M | 75168
291 | 200 | Cost of Pipes and slabs-Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | elect | supply | SMR40077 | 363 | M | 72600
292 | 10 | Cost of Pipes and slabs-Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | elect | labour | SMR40085 | 484 | EA | 4840
293 | 5 | Load-11/33KV XLPE UG Cable for all sizes | elect | labour | SWR11230 | 1024 | DR | 5120
294 | 5 | Unload-11/33KV XLPE UG Cable for all sizes | elect | labour | SWR11231 | 1024 | DR | 5120
295 | 24 | Making of Outdoor/Indoor End Termination-Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | elect | labour. | SWR10391 | 2370.63 | EA | 56895.12
296 | 6 | UG Cables Joints Making of Straight through joints-11 KV 3x300 Sqmm Cable | elect | labour. | SWR10386 | 3725.45 | EA | 22352.7
297 | 1.1 | Loading of M.S.Channels, Angles, Flats & Rods etc., | elect | labour | SWR10206 | 221 | TO | 243.1
298 | 1.1 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | elect | labour | SWR10524 | 185 | TO | 203.5
299 | 1.1 | Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading)-Above 50 KM and upto 80 KM | elect | labour. | SWR10151 | 718.08 | TO | 789.888
300 | 1.1 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | elect | labour | SWR10869 | 3426 | TO | 3768.6
301 | 50 | Supply of Danger boards with clamps | elect | supply | SMR40070 | 116 | EA | 5800
302 | 6 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | elect | labour | SWR12331 | 146.63 | EA | 879.78
303 | 6 | Loading of 11KV AB Switch Conventional type | elect | labour | SWR10238 | 80 | EA | 480 |  |  | 3603796.51
304 | 6 | Un loading of 11KV AB Switch Conventional type | elect | labour | SWR10556 | 80 | EA | 480 |  |  | 2170959.76
305 | 10 | S&E-Smart RFID marker | elect | labour | SWR25089 | 2745 | EA | 27450 |  |  | 2907536.6
Sub Total: | [7 empty] | 8661442.3156 |  |  | 8682292.87
18% Service tax on labour: | [7 empty] | 1559059.6168
Total Rs. | [7 empty] | 10220501.9324 | 10220501.918 | 0.014408
WBS. No. S-1793-13-07-01-01-001
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 135.61 | Earth work excavation in all type of ordinary soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | m3 | 65906.46
3 | 32.45 | Plain Cement concrete PCC (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4797 | m3 | 155662.65
4 | 117.88 | Coursed Rubble stone (CRS) masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4910 | m3 | 578790.8
6 | 3.564 | RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-chargeRCC M20 Grade footing 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33098 | 9549 | m3 | 34032.636
7 | 2.28 | RCC M20 Grade Coloumn . 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33100 | 13298 | m3 | 30319.44
8 | 2.25 | RCC M20 Grade Plinth beams 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33099 | 12419 | m3 | 27942.75
9 | 3.17 | D) RCC M20 Grade Roof Beams landing beam 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33121 | 12336 | m3 | 39105.12
10 | 0.58 | e)RCC M20 Grade Lintels 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33107 | 13127 | m3 | 7613.66
11 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33114 | 1380 | m2 | 3726
12 | 15.224 | g) RCC M20 Grade Roof Slab for Control Room 'RCC 1:1.5:3 nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials, labour, scaffolding, centering, machine mixing, vibrating, curing all leads and lifts,seignarage charges in all positions of the building but excluding cost of steel and its fabrication for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33128 | 10923 | m3 | 166291.752
13 | 3 | Reinforcement steelSupplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | Ton | 212061
14 | 38.36 | Brick masonry in cement mortar CM (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work | Civil | Labour | SWR33068 | 8296 | m3 | 318234.56
15 | 2.7 | Plain Cement concrete PCC (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6166 | m3 | 16648.2
16 | 606.06 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 565 | m2 | 342423.9
17 | 349.515 | Painting with two coats of Plastic Emulsn paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | m2 | 73398.15
18 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | m2 | 17072.25
19 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | m2 | 12978
20 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
22 | 90 | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
23 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
24 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
25 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
26 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
27 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
28 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
29 | 80 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 86560
30 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
31 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
32 | 290 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 52200
33 | 1 | Supply and erecting D.O.L Starter 415V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
34 | 305 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | m | 58560
35 | 71 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | m | 29110
36 | 35 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 16310
37 | 839.38 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | m3 | 259368.42
38 | 16.56 | Providing Design R.C.M. drop wall of 25mm thickness with cm 1:3 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3130 | m2 | 51832.8
39 | 12.24 | Supply and fixing of Ms ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | m2 | 36597.6
40 | 5.91 | Supply and fixing of doors with the MT Wood frames of the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | m2 | 43225.74
41 | 128.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 126 | m2 | 16159.5
42 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | m2 | 31302.72
43 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | m2 | 15135.84
44 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 788 | m2 | 96072.96
45 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 878 | m2 | 5917.72
46 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | m2 | 35578.74
47 | 101.17 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 587 | m2 | 59386.79
48 | 60 | Supply & fixing of 25mm dia 2mm thick suSupply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | m | 6480
49 | 1 | Supply & fixing TPN Distribution board w Supply & fixing TPN Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
50 | 10 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
51 | 6 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
52 | 24 | Supply and Fixing of modular switch, LP,FP,EFP Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
53 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
54 | 1 | Supply of 12" (300mm)ISI, 900 RPM Heavy duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
55 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | m | 13500
56 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | m | 18540
57 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
58 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
59 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
60 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
61 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | m | 26425
62 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
63 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
64 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
65 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | m | 5544
66 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | m | 7380
67 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
68 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34312 | 2228 | EA | 2228
69 | 6 | Supply & fixing 15 mm angle stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
70 | 4 | S&F 15 mm N.P bib tap Indian make 400 grams full turn Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
71 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
72 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
73 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
74 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
75 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
76 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | m | 10755
77 | 200 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | m | 62600
78 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
79 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
80 | 36 | Plain Cement concrete PCC (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 5087 | m3 | 183132
81 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | m2 | 277200
82 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
83 | 222.2468 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | m3 | 8889.873
84 | 725.7496 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | m3 | 70760.585
85 | 839.38 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | m3 | 25181.4
86 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33405 | 1444 | EA | 86640
87 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | Swr33408 | 16 | m | 19200
4231751.016
|  |  | 18% GST Rs. |  |  |  |  | 761715.1829
|  |  | Grand Total Rs. |  |  |  |  | 4993466.1989
[6 empty] | Total civil+Electrical |  | 12893193.3316