## T-2532-14-05-11-01-001 BIFURCAT
SCHEDULE
NAME OF THE WORK:Estimate for bifurcation of 11KV Yamnampet feeder loads by laying of 11 KV 3X300 Sq.mm XLPE UG cable UG cable (Double Run) for a distance of420Mtrs duly diverting load from 11 KV Yamnampet feeder from 33/11KV Ghatkesar SS to the new 11KV Ismailkhanguda feeder emanating from33/11KV 2BHK SS in Ghatkesar section in Ghatkesar subdivision of Keesara Division in Habsiguda Circle under T&D Improvements to original works (Summer Action Plan works-2026). T-2532-14-05-11-01-001
Sl. No. | SSR CODE | Qty | Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate in Rs. | Unit | NET PRICE
1 | SWR11981 | 100 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV 3x300 Sqmm Cable | Electrical work | Lay-DR 11KV 3x300sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 1264.64 | M | 126464
2 | SWR11001 | 200 | HDD (Horizontal Directional Drilling) in normal soil, Laying of 33&11KV UG cable by HDD method with casing HDPE pipe of 160mm PN4 PE 80 as per IS4984 | Electrical work | HDD cable with HDPE pipe in Hard rock | As per relevent standard specification | 6993 | M | 1398600
3 | SWR12005 | 20 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) 11 KV 3x300 Sqmm Cable | Electrical work | Raise-DR 11KV 3x300sqmm UG Cb on support | As per relevent standard specification | 275.4 | M | 5508
4 | SWR10391 | 4 | Making of Outdoor/Indoor End Termination Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Electrical work | OD/Idoor end termination 11kv 3x300 xlpe | As per relevent standard specification | 2370.63 | EA | 9482.52
5 | SWR10386 | 2 | Making of Straight through joints 11 KV 3x300 Sqmm Cable | Electrical work | Straight through joint 11kv 3x300 xlpe | As per relevent standard specification | 3725.45 | EA | 7450.9
6 | SMR40082 | 48 | Supply of 9" B class GI pipe | Electrical work | S-9" B Class GI pipe 7.3mm thck 28.8Kg/M | As per relevent standard specification | 1113 | M | 53424
7 | SMR11484 | 4 | Supply of CI eath pipe with 50mm dia,2.0 M Length | Electrical work | S-CI Pipe earthing 50mm dia 2m long | As per relevent standard specification | 2441 | EA | 9764
8 | SWR10359 | 4 | Providing of RCC collar to earth pit, Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Earth work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 1544
9 | SWR10357 | 4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 4936.8
10 | SWR12125 | 40 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Electrical work | Run-GI Earth Flat 25x3mm from metallic p | As per relevent standard specification | 14.03 | M | 561.2
11 | SMR11485 | 24 | Supply of earthing pipe with materials of GI Flat 25X3 mm | Electrical work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 2520
12 | SMR11488 | 20 | Supply of GI Bolts & Nuts etc | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 2350
13 | SWR11039 | 2 | 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Earth work | Exca Hard pit w/o blast 0.76X0.76X1.83M | As per relevent standard specification | 928 | EA | 1856
14 | SWR11266 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, for RS Joist, Rail poles Supply & Fabrication of bottom plate with 6mm thichness and for Box poles Supply & Fabrication of Top & Bottom plate with 6mm thichness Box pole 9/10/11 Mtr | Electrical work | Erection of 9/10/11Meter Box pole | As per relevent standard specification | 2643.83 | EA | 5287.66
15 | SWR10642 | 2 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable, Painting of RS Joist on inner phasing with red Oxide before Joining as box pole | Electrical work | Fabricate&Paint-175x85/150x75mm RS Joist | As per relevent standard specification | 512.55 | EA | 1025.1
16 | SWR10640 | 2 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Electrical work | Painting of RS Joist(1C RO, 2C Al.Paint) | As per relevent standard specification | 1132 | EA | 2264
17 | SWR10356 | 2.2 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 14473.8
18 | SWR11890 | 0.062 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 241.37
19 | SWR25089 | 2 | S&E-Smart RFID marker | Electrical work | S&E-Smart RFID marker | As per relevent standard specification | 2745 | EA | 5490
20 | SMR40085 | 2 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , TGSPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Earth work | S-RCC Cable Joint/Route Marker | As per relevent standard specification | 484 | EA | 968
21 | SWR12101 | 2 | Painting of feeder name on support including cost of paint | Electrical work | Paint-Feeder Name on Support incl. Paint | As per relevent standard specification | 53 | EA | 106
22 | SWR11862 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, Battery Chargers with Batteries, RMU, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 20 Km and upto 30 Km with Lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 7382.76
23 | SWR10133 | 1.1 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 20 KM and upto 30 KM | Electrical work | TRANSPORT OF STEEL 20 TO 30KM | As per relevent standard specification | 476.34 | TO | 523.97
24 | SWR11873 | 20 | MS Channel 75 x 40 mm | Electrical work | Cutting Charges-MS Channel 75x40mm | As per relevent standard specification | 9 | EA | 180
25 | SWR11230 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Electrical work | Load-11/33KV XLPE UG Cable for all sizes | As per relevent standard specification | 1024 | DR | 2048
26 | SWR11231 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Electrical work | Unload-11/33KV XLPE UG Cable all sizes | As per relevent standard specification | 1024 | DR | 2048
27 | SWR11171 | 4 | Loading of 33/11KV XLPE UG Cable End Termination Kits for all sizes | Electrical work | Loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 6 | EA | 24
28 | SWR11152 | 4 | Un loading of 33/11KV XLPE UG Cable End Termination Kits for all sizes | Electrical work | Un-loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 4 | EA | 16
29 | SWR11172 | 2 | Loading of 33/KV XLPE UG CableStraight Through Joint Kits for all sizes | Electrical work | Loading 11/33KV Straight thr jointkit | As per relevent standard specification | 8 | EA | 16
30 | SWR11153 | 2 | Un loading of 33/KV XLPE UG CableStraight Through Joint Kits for all sizes | Electrical work | Un-loading 11/33KV Straight thr jointkit | As per relevent standard specification | 4 | EA | 8
31 | SWR10204 | 4 | Loading of R.S. Joists 175 x 85 mm | Electrical work | LOADING of R.S. Joists 175 x 85 mm | As per relevent standard specification | 76 | EA | 304
32 | SWR10522 | 4 | Un loading of R.S. Joists 175 x 85 mm | Electrical work | UNLOADING of R.S. Joists 175 x 85 mm | As per relevent standard specification | 50 | EA | 200
33 | SWR11973 | 220 | Excavation & laying of UG Cable (Double Run)Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV 3x300 Sqmm Cable | Electrical work | Lay-DR 11KV 3x300sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 631.06 | M | 138833.2
| Total service cost | [7 empty] | 1805901.28
18% GST on service cost | [8 empty] | 325062.2304
Total with GST | [8 empty] | 2130963.5104
s