## Sheet1
SOUTHERN POWER DISTRIBUTION COMPANY OF TELANGANA LTD.
Name of the work: Bifurcation of loads from 33KV Mannapur feeder emanating from 132/33KV Zaheerabad EHT SS by erection of 12.25KM 33KV line from 132/33KV Zaheerabad EHT SS to 33/11KV Mannapur SS which involves laying of 0.25KM 33KV 3X400sq.mm XLPE UG cable (Double Run) and stringing of 12KM 33KV SCOH line with 100sq.mm AAA conductor over now proposed 12.5Mtrs/11Mtrs Poles in Mannapur Section of Zaheerabad Town Sub-Division of Zaheerabad Division in Sangareddy Circle under T&D Improvements to original works (Summer Action Plan-2026).T-2530-90-06-01-01-001
S NO | SSR CODES | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR22092 | 12.3 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 9409.5
2 | SWR10108 | 130 | Excavation of Pole pits of size 0.75x0.9x1.95 Mts' for 11.0 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock not Requiring blasting. | Earth work | EXCAV. OF PIT 0.75 M x 0.9 M x 1.95 M | As per relevent standard specification | 720 | EA | 93600
3 | SWR11040 | 60 | Excavation of Pole pits of size 0.75x0.9x1.95 Mts' for 11.0 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock not requiring blasting. | EArth work | Ex of Hard pit w/o blast 0.75X0.9X1.95M | As per relevent standard specification | 883.58 | EA | 53014.8
4 | SWR10978 | 190 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit exc | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 791403.2
5 | SWR11083 | 40 | Erection of9.1 Mts PSCC poles for stuts in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Erec of 9.1 Mts PSCC poles for stuts | As per relevent standard specification | 2400 | EA | 96000
6 | SWR10981 | 27 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 47506.5
7 | SWR10356 | 117.58 | Concreting the location after erection of 12.5mts/11.0 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.75X0.75X2 Mts)* 104 = 117.58 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 773558.82
8 | SWR10356 | 51.2 | Concreting the location after erection of 11mts /9.1 mt stud pole and stay set pit with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.45X0.45X1.265 Mts)* 202 = 51.2 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 336844.8
9 | SWR10366 | 10.5 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 132300.63
10 | SMR11488 | 600 | Supply of MS Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 70500
11 | SWR11180 | 190 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 82074.3
12 | SWR20308 | 40 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 16291.6
13 | SWR10191 | 10 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 2020
14 | SWR10509 | 10 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 1000
15 | SWR11863 | 5 | Transport of Conductor drum, VCB etc, above 10 KM and upto 50 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >30 & <50Km | As per relevent standard specification | 4372.74 | EA | 21863.7
16 | SWR10134 | 8.9 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 5228.928
17 | SWR10206 | 8.9 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 1966.9
18 | SWR10524 | 8.9 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 1646.5
19 | SWR10211 | 70 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 210
20 | SWR10529 | 70 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 210
21 | SWR12416 | 20 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | KI | 40
22 | SWR10631 | 20 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 40
23 | SWR10618 | 20 | Loading of 33KV Metal parts bag of 25 nos | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 1300
24 | SWR10632 | 20 | Unloading of 33 KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 1300
25 | SWR10322 | 144 | Fabrication of Stay clamps with 75x8 mm Flat including 2 coats of Red oxide painting | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevent standard specification | 42.84 | EA | 6168.96
26 | SWR10378 | 300 | Painting of Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 9600
27 | SWR10354 | 144 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 98572.32
28 | SWR21190 | 144 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 74880
29 | SWR10109 | 70 | Excavation of Pole pits of size 0.92x0.92x2.3 Mts' for 12.50 mts spun PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock not Requiring blasting. | Earth work | EXCAVATION OF PIT(3.0" x 3.0" x 7.6") | As per relevent standard specification | 842.78 | EA | 58994.6
30 | SWR10704 | 1.5 | Paving out and stringing of 100sqmm 33/11kv Line 6 Cond Double circuit line by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location | Electrical work | Stringing 100sqmm 33/11kv Line 6 Cond DC | As per relevent standard specification | 24606.13 | KM | 36909.195
31 | SWR10319 | 260 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31.62 | EA | 8221.2
32 | SWR10350 | 70 | Erection of Spun poles 12.5 Mtrs / 12.9Mtrs PSCC in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Erection of Spun pole 12.5Mt | As per relevent standard specification | 4115.7 | EA | 288099
33 | SWR10294 | 130 | Cutting Charges for MS chanl 100x50mm | Electrical work | Cutting Charges for MS chanl 100x50mm | As per relevent standard specification | 10 | EA | 1300
34 | SWR10296 | 130 | Cutting Charges for MS angle all sizes | Electrical work | Cutting Charges for MS angle all sizes | As per relevent standard specification | 7 | EA | 910
35 | SWR11980 | 250 | Laying of 33KV XLPE 3x400sqmm UG Cable Double Run Along the CC / BT multi layer road requiring compressor including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs | Electrical work | Lay-DR 33KV 3x400sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 1388.84 | M | 347210
36 | SWR12004 | 50 | Raising of 33KV XLPE 3x400sqmm UG Cable Double Run on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Electrical work | Raise-DR 33KV 3x400sqmm UG Cb on support | As per relevent standard specification | 323.85 | M | 16192.5
37 | SWR10387 | 4 | Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination | Electrical work | OD/Idoor end termination 33kv 3x400 xlpe | As per relevent standard specification | 2764.76 | EA | 11059.04
38 | SMR11483 | 12 | Supply of CI eath pipe with 80mm dia,2.0 M Length | Electrical work | S-CI Pipe earthing 80mm dia 2.75m long | As per relevent standard specification | 2789 | EA | 33468
39 | SWR11230 | 2 | loading of 11KV/33KV XLPE UG Cable for all size | Electrical work | Load-11/33KV XLPE UG Cable for all sizes | As per relevent standard specification | 1024 | DR | 2048
40 | SWR11231 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all size | Electrical work | Unload-11/33KV XLPE UG Cable all sizes | As per relevent standard specification | 1024 | DR | 2048
41 | SWR10642 | 2 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Electrical work | Fabricate&Paint-175x85/150x75mm RS Joist | As per relevent standard specification | 512.55 | EA | 1025.1
42 | SWR10640 | 2 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Electrical work | Painting of RS Joist(1C RO, 2C Al.Paint) | As per relevent standard specification | 1132 | EA | 2264
43 | SWR10357 | 12 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 14810.4
44 | SWR10359 | 12 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Earth work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 4632
45 | SWR10204 | 2 | LOADING of R.S. Joists 175 x 85 mm | Electrical work | LOADING of R.S. Joists 175 x 85 mm | As per relevent standard specification | 76 | EA | 152
46 | SWR10522 | 2 | UNLOADING of R.S. Joists 175 x 85 mm | Electrical work | UNLOADING of R.S. Joists 175 x 85 mm | As per relevent standard specification | 50 | EA | 100
47 | SWR11890 | 0.064 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Electrical work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3892.97 | M3 | 249.1501
48 | SWR11266 | 2 | Erection of 9/10/11Meter Box pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Erection of 9/10/11Meter Box pole | As per relevent standard specification | 2643.83 | EA | 5287.66
49 | SWR10392 | 5 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 22500
50 | SWR10239 | 5 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | ELectrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 630
51 | SWR10557 | 5 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | ELectrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 395
52 | SMR11485 | 120 | Supply of earthing GI Flat 25X3 mm including material | Earth work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 12600
53 | SWR11185 | 70 | Sub Transport of 11/12.5/12.9M Spun poles (Including loading and unloading) upto 10KM | Electrical work | SubTrnsprt any Spun Pole incl. L&UL<10KM | As per relevent standard specification | 771.38 | EA | 53996.6
54 | SWR10107 | 40 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 9.1 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In Hard Gravel and Hard murram not requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 28000
55 | SWR10988 | 250 | Laying of the 2nd Cable in Excavated Trench along the footpath through 225mm dia GI pipe for 33KV, 150mm dia GI pipe for 11KV (excluding the cost of GI pipe) | Electrical work | Lay-2nd Cable in Excavated Trench | As per relevent standard specification | 204.1 | M | 51025
Total | [8 empty] | 3732677.9031
18 % GST on labour | [8 empty] | 671882.0226
Grand Total | [8 empty] | 4404559.9256