## with out road cutting
Schedule (WBS No.E-2025-07-02-13-04-065)
E-Procurement Schedule proposal for "extension of 11KV HT Supply for Addl load of 500KVA CMD without change in CL over and above the existing 2500KVA CMD with a CL 4000HP making total Load 3000KVA CMD with a CL 4000HP under Cat-IX to M/s. DEPOT MANAGER TSRTC, (MCL3148) at TGRTC Miyapur-II Depot in Miyapur Section of Miyapur Sub-Division in Kukatpally Division of Medchal Circle under Capital Works.
11KV Line Work.
Sl.No. | SSR CODES | Estimate Quantity (Only figures) | Particulars | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item Short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals) | `
1 | SMR11488 | 20 | Supply of GI Bolts & Nuts etc | Erection work | Supply of work | As per relevent standard specification | 117.5 | KG | 2350
2 | SWR10107 | 1 | Excavation of pits in all soils except hard rock requiring blasting :0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Erection work | Erection work | As per relevent standard specification | 700 | EA | 700
3 | SWR10356 | 1.05 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Erection work | Erection work | As per relevent standard specification | 6579 | M3 | 6907.95
4 | SWR10357 | 4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height . | Erection work | Erection work | As per relevent standard specification | 1234.2 | EA | 4936.8
5 | SMR11485 | 75 | Supply of GI Flat 25X3 mm | Erection work | Supply of work | As per relevent standard specification | 105 | KG | 7875
6 | SWR23214 | 1000 | Power Interruption Charges | Erection work | Erection work | As per relevent standard specification | 7 | KWH | 7000
7 | SMR40132 | 200 | Supply of 120 Sqmm Aluminium lugs | Erection work | Supply of work | As per relevent standard specification | 12.52 | EA | 2504
8 | SWR11267 | 1 | Erection of Box pole 12 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Erection work | Erection work | As per relevent standard specification | 3901.37 | EA | 3901.37
9 | SWR11973 | 1900 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. : 11KV 3x300sqmm UG Cable HG/BC/CC/BT | Erection work | Erection of work | As per relevent standard specification | 631.06 | M | 1199014
10 | SWR10391 | 56 | Making of Outdoor/Indoor End Termination 11kv 3x300 xlpe ug cable | Supply work | Erection of work | As per relevent standard specification | 2370.63 | EA | 132755.28
11 | SWR11119 | 1 | Testing of HT TVR Meter at site | Erection work | Erection of work | As per relevent standard specification | 246 | EA | 246
12 | SWR10522 | 2 | UNLOADING of R.S. Joists 175 x 85 mm | Erection work | Erection of work | As per relevent standard specification | 50 | EA | 100
13 | SWR10204 | 2 | LOADING of R.S. Joists 175 x 85 mm | Erection work | Erection of work | As per relevent standard specification | 76 | EA | 152
14 | SWR10642 | 2 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable, Painting of RS Joist on inner phasing with red Oxide before Joining as box pole | Erthing work | Erthing of work | As per relevent standard specification | 512.55 | EA | 1025.1
15 | SWR10640 | 2 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Erection work | Erection of work | As per relevent standard specification | 1132 | EA | 2264
16 | SWR21530 | 1 | Installation,site test & commissioning of AMR hardware | Supply work | Erection of work | As per relevent standard specification | 350 | EA | 350
17 | SWR25245 | 100 | Centage Chrgs-16.5% on SWR25212 | Supply work | Erection of work | As per relevent standard specification | 750.75 | M2 | 75075
18 | SWR11230 | 14 | Loading of 11/33KV XLPE UG Cable for all sizes | Supply work | Erection of work | As per relevent standard specification | 1024 | DR | 14336
19 | SWR11231 | 14 | Unloading of 11/33KV XLPE UG Cable all sizes | Supply work | Erection of work | As per relevent standard specification | 1024 | DR | 14336
20 | SWR12005 | 100 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) :11KV 3x300sqmm UG Cb | Supply work | Erection of work | As per relevent standard specification | 275.4 | M | 27540
21 | SWR10664 | 3 | Erection of 11KV 3 Way RMU | Erection work | Erection of work | As per relevent standard specification | 2051.48 | EA | 6154.44
22 | SWR10615 | 3 | LOADING of 11KV 3 Way RMU | Erection work | Erection of work | As per relevent standard specification | 907.8 | EA | 2723.4
23 | SWR10629 | 3 | UNLOADING of 11KV 3 Way RMU | Erection work | Erection of work | As per relevent standard specification | 907.8 | EA | 2723.4
24 | SWR20871 | 3 | Construction of plinth for 3way RMUs etc | Supply work | Erection of work | As per relevent standard specification | 6000 | EA | 18000
25 | SMR11483 | 4 | Supply of CI Pipe earthing 80mm dia 2.75m long | Supply work | Supply of work | As per relevent standard specification | 2789 | EA | 11156
26 | SWR10359 | 4 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Supply work | Erection of work | As per relevent standard specification | 386 | EA | 1544
27 | SWR10386 | 12 | Straight through joint 11kv 3x300 xlpe | Erection work | Erection of work | As per relevent standard specification | 3725.45 | EA | 44705.4
Total Amount | [8 empty] | 1590375.14
|  |  | 11KV line | 1590375.14
|  |  | Total Amount | 1590375.14
|  |  | Gst@18% | 286267.5252
|  |  | Total Amount | 1876642.6652