## sp. 35
SCHEDULE (T.Sp.No. 34 /2025-26)
Name of the Work :- Shifting of 33kV, 11kV & LT UG Cables & OH Lines from Ali Café, Amberpet to Spice Restaurant, Moosarambagh by laying of 33kV 3X400Sq.mm XLPE UG cable, 11kV 3X300Sq.mm XLPE UG cable on request of Executive Engineer, PD-NZ, GHMC after completion of Construction of New High Level Bridge at Moosarambagh on Moosi River in Master Plan Sub-Division-III, Division-II in Hyderabad Circle under GHMC-DC works (Reserved For SC Category).
WBS Element :- G-2025-12-02-03-01-001
Sl No | Quantity | Description of item | Work Type | Item Short Description | SAP Code | Rate (INR) | UOM | AMOUNT (Rs.)
1 | 1 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 765
2 | 28 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 28672
3 | 14 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11860 | 2720.34 | EA | 38084.76
4 | 28 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 28672
5 | 200 | Excavation & laying of UG Cable (Double Run) - Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc - (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.- Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11980 | 1388.84 | M | 277768
6 | 150 | Excavation & laying of UG Cable (Four Run) - Laying of XLPE UG cable Four Run including excavation of trench of size 1050mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc - (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.- Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR12040 | 2103.75 | M | 315562.5
7 | 300 | Excavation & laying of UG Cable (Six Run) - Laying of XLPE UG cable Six Run including excavation of trench of size 1050mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc - (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.- Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR12069 | 2314.13 | M | 694239
8 | 80 | Excavation & laying of UG Cable (Six Run) - Laying of XLPE UG cable Six Run including excavation of trench of size 1050mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc - (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.- Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR12073 | 2594.63 | M | 207570.4
9 | 5000 | Laying of Second 33KV UG Cb in Existing Duct | Elect | Labour | SWR12452 | 200 | M | 1000000
10 | 2550 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 520455
11 | 20 | S&E-Smart RFID marker | Elect | Supply | SWR25089 | 2745 | EA | 54900
12 | 30 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 171023.4
13 | 1000 | Supply of 6" B class GI pipe 150 NB GI Pipe 4.85 mm thickness, 19.2 KG/Mtr | Elect | Supply | SMR40081 | 1344 | M | 1344000
14 | 8 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 22118.08
15 | 40 | Raising of double run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR12004 | 323.85 | M | 12954
16 | 650 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 19500
17 | 0.25 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 55.25
18 | 0.25 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) upto 10KM | Elect | Labour | SWR10147 | 332.52 | TO | 83.13
19 | 0.25 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 46.25
20 | 2 | Supply of M+3 Tower (Galvanized) | Elect | Supply | SMR11683 | 140674.3 | EA | 281348.6
21 | 2 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) | Elect | Supply | SMR11684 | 28520.64 | EA | 57041.28
22 | 9.504 | Earth work excavation of pits in hard rock requiring blasting.(wherever feasible/ required) | Elect | Labour | SWR20769 | 1012.35 | M3 | 9621.3744
23 | 2 | Erection of M+3 Tower (Galvanized) | Elect | Labour | SWR11850 | 64576 | EA | 129152
24 | 2 | Erection of Extension of 3Mtrs for M+3 (Galvanized) | Elect | Labour | SWR11851 | 5168.95 | EA | 10337.9
25 | 2 | Formation of Cut point for 33 KV Double circuit line excluding pole erection and stays | Elect | Labour | SWR10466 | 3198.72 | EA | 6397.44
26 | 4 | Supply of CI eath pipe with 80mm dia,2.75 M Length | Elect | Supply | SMR11483 | 2789 | EA | 11156
27 | 4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 4936.8
28 | 4 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 1544
29 | 2 | Dismantleing Rail pole 90 lbs | Elect | Labour | SWR11322 | 900 | EA | 1800
30 | 0.2 | Dismantling of 100 Sqmm Conductor DC Line. | Elect | Labour | SWR22064 | 11816.7 | KM | 2363.34
31 | 2 | Dismantling of M type tower | Elect | Labour | SWR11122 | 3484 | EA | 6968
32 | 2.802 | LOADING of MS Scrap | Elect | Labour | SWR10258 | 578 | TO | 1619.556
33 | 2.802 | UNLOADING of MS Scrap | Elect | Labour | SWR10576 | 578 | TO | 1619.556
34 | 0.181 | LOADING of ACSR conductor scrap | Elect | Labour | SWR10257 | 490.99 | TO | 88.8692
35 | 0.181 | UNLOADING of ACSR conductor scrap | Elect | Labour | SWR10575 | 490.99 | TO | 88.8692
36 | 2.983 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10148 | 481.44 | TO | 1436.1355
37 | 41.67 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 1708.47
38 | 0.15 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 513.9
39 | 4 | Dimantling of Extension of M+3 Tower | Elect | Labour | SWR12480 | 2584.48 | EA | 10337.92
40 | 14 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 14336
41 | 7 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excludingof loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 23097.9
42 | 14 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 14336
43 | 150 | Excavation & laying of UG Cable (Triple Run ) - Laying of 11 KV 3x300 Sqmm XLPE UG cable Triple Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 1050mm for 11 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - Along the CC / BT multi layer road requiring compressor - 11 KV 3x300 Sqmm Cable | Elect | Labour | SWR12020 | 1578.45 | M | 236767.5
44 | 250 | Excavation & laying of UG Cable (Double Run) - Laying of 11 KV 3x300 Sqmm Cable Double Run including excavation of trench of size 600mm and wide1050mm for 11 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc.. (Second cable laying cost not Included) depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Along the CC / BT multi layer road requiring compressor - 11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11981 | 1264.64 | M | 316160
45 | 350 | Excavation & laying of UG Cable in Single Run - Laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc..depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - Along the CC / BT multi layer road requiring compressor-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11928 | 1073.94 | M | 375879
46 | 2500 | Laying of Second 33KV UG Cb in Existing Duct | Elect | Labour | SWR12452 | 200 | M | 500000
47 | 550 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 112255
48 | 14 | Making of 11 KV 3x300 Sqmm Cable Straight through joints | Elect | Labour | SWR10386 | 3725.45 | EA | 52156.3
49 | 650 | Supply 6" B Class GI pipe 5mm thck 20Kg/M | Elect | Supply | SMR40081 | 1344 | M | 873600
50 | 50 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 50600
51 | 8 | Making of 11 KV 3x300 Sqmm Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10391 | 2370.63 | EA | 18965.04
52 | 60 | Raising of Double run 11 KV 3x300 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR12005 | 275.4 | M | 16524
53 | 40 | Raising of Single run 11 KV 3x300 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11955 | 144.08 | M | 5763.2
54 | 0.75 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 165.75
55 | 0.75 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 138.75
56 | 2 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 152
57 | 1.25 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 515.1
58 | 2 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 100
59 | 2 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 1025.1
60 | 2 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 2264
61 | 1 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 990.68
62 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 5568
63 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 2643.83
64 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - 9.1M PSCC Pole | Elect | Labour | SWR10343 | 2400 | EA | 14400
65 | 84 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 3444
66 | 5.32 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 35000.28
67 | 0.031 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3892.9 | M3 | 120.6799
68 | 0.75 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2569.5
69 | 5 | Supply of CI eath pipe with 80mm dia,2.75 M Length | Elect | Supply | SMR11483 | 2789 | EA | 13945
70 | 5 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 6171
71 | 5 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 1930
72 | 10 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 4840
73 | 1 | RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elect | Labour | SWR21843 | 25967.57 | EA | 25967.57
74 | 1 | Erection of Three Phase DTRs | Elect | Labour | SWR10463 | 1139.95 | EA | 1139.95
75 | 1 | Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10238 | 80 | EA | 80
76 | 1 | Un loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10556 | 80 | EA | 80
77 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR20102 | 1813.49 | EA | 1813.49
78 | 1 | Loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10231 | 18 | EA | 18
79 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
80 | 1 | Un loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10549 | 18 | EA | 18
81 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 740.52 | SET | 740.52
82 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elect | Labour | SWR10674 | 1594.67 | EA | 1594.67
83 | 0.3 | Stringing of LT AB cable 3x70 + 1x16 + 1x50 | Elect | Labour | SWR10666 | 8450 | KM | 2535
84 | 6 | Supply of Suspension Clamp Assembly & Eye Hook-M | Elect | Supply | SMR11492 | 65 | EA | 390
85 | 6 | Erection of Suspension Clamp Assemb &Eye hook-L | Elect | Labour | SWR12512 | 8 | EA | 48
86 | 2 | Supply of Dead End Clamp Assembly & Eye Hook-M | Elect | Supply | SMR11493 | 80 | EA | 160
87 | 2 | Erection of Dead End Clamp Assemb & Eye hook-L | Elect | Labour | SWR12513 | 8 | EA | 16
88 | 1 | Dismantle of 3-Ph DTR ( Upto 160 KVA) | Elect | Labour | SWR11729 | 975.12 | EA | 975.12
89 | 1 | Dismantle-3Ph 100KVA DTR Plinth | Elect | Labour | SWR12198 | 1160.25 | EA | 1160.25
90 | 1 | Dismantle of 11KV AB Switch TT Type | Elect | Labour | SWR12172 | 889.73 | EA | 889.73
91 | 5 | Dismantle of 9.1 M long PSCC pole | Elect | Labour | SWR11320 | 948.09 | EA | 4740.45
92 | 1 | Dismantle of Box pole 9/10/11 Mtr | Elect | Labour | SWR11329 | 1130 | EA | 1130
93 | 0.2 | Dismantling of 11kV 34/ 55 Sqmm SC Line | Elect | Labour | SWR22065 | 4500 | KM | 900
94 | 50 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 5875
95 | 1 | Dismantle of LT distribution box | Elect | Labour | SWR20075 | 669.38 | EA | 669.38
96 | 1 | Dimantle of 11KV HG Fuse Set incl earthing | Elect | Labour | SWR11745 | 353.43 | SET | 353.43
97 | 1 | LOADING of 11KV 5 Way RMU | Elect | Labour | SWR10616 | 1268.63 | EA | 1268.63
98 | 1 | UNLOADING of 11KV 5 Way RMU | Elect | Labour | SWR10630 | 1268.63 | EA | 1268.63
99 | 1 | Construction of plinth for mount. new 5Way RMU | Elect | Labour | SWR10731 | 8000 | EA | 8000
100 | 1 | Erection of 5-Way RMU | Elect | Labour | SWR11069 | 2783.33 | EA | 2783.33
101 | 2 | Supply of CI eath pipe with 50mm dia,2.0 M Length | Elect | Supply | SMR11484 | 2441 | EA | 4882
102 | 20 | Supply of GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 2100
103 | 33.33 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Elect | Labour | SWR12125 | 14.03 | M | 467.6199
104 | 2 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 2468.4
105 | 2 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 772
106 | 2 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 106
Total (Excl.GST) in Rs: | [7 empty] | 8061683.2601
GST @ 18 % | [7 empty] | 1451102.9868
Total (Incl. GST) in Rs: | [7 empty] | 9512786.2469
* The work will be taken up after completion of GHMC high level Bridge on Musi River at Moosarambagh ( The GHMC authorities provided Utility Duct on Bridge)

## 002 (2)
SCHEDULE
Name of the Work :- Shifting of 33kV, 11kV & LT UG Cables & OH Lines from Ali Café, Amberpet to Spice Restaurant, Moosarambagh by laying of 33kV 3X400Sq.mm XLPE UG cable, 11kV 3X300Sq.mm XLPE UG cable on request of Executive Engineer, PD-NZ, GHMC after completion of Construction of New High Level Bridge at Moosarambagh on Moosi River in Master Plan Sub-Division-III, Division-II in Hyderabad Circle under GHMC-DC works
WBS Element :- G-2025-12-02-03-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 1 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 765
2 | 28 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 28672
3 | 14 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11860 | 2720.34 | EA | 38084.76
4 | 28 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 28672
5 | 200 | Excavation & laying of UG Cable (Double Run) - Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc - (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.- Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11980 | 1388.84 | M | 277768
6 | 150 | Excavation & laying of UG Cable (Four Run) - Laying of XLPE UG cable Four Run including excavation of trench of size 1050mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc - (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.- Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR12040 | 2103.75 | M | 315562.5
7 | 300 | Excavation & laying of UG Cable (Six Run) - Laying of XLPE UG cable Six Run including excavation of trench of size 1050mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc - (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.- Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR12069 | 2314.13 | M | 694239
8 | 80 | Excavation & laying of UG Cable (Six Run) - Laying of XLPE UG cable Six Run including excavation of trench of size 1050mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc - (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.- Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR12073 | 2594.63 | M | 207570.4
9 | 5000 | Laying of Second 33KV UG Cb in Existing Duct | Elect | Labour | SWR12452 | 200 | M | 1000000
10 | 2550 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 520455
11 | 20 | S&E-Smart RFID marker | Elect | Supply | SWR25089 | 2745 | EA | 54900
12 | 30 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 171023.4
13 | 1000 | Supply of 6" B class GI pipe 150 NB GI Pipe 4.85 mm thickness, 19.2 KG/Mtr | Elect | Supply | SMR40081 | 1344 | M | 1344000
14 | 8 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 22118.08
15 | 40 | Raising of double run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR12004 | 323.85 | M | 12954
16 | 650 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 19500
17 | 0.25 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 55.25
18 | 0.25 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) upto 10KM | Elect | Labour | SWR10147 | 332.52 | TO | 83.13
19 | 0.25 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 46.25
20 | 2 | Supply of M+3 Tower (Galvanized) | Elect | Supply | SMR11683 | 140674.3 | EA | 281348.6
21 | 2 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) | Elect | Supply | SMR11684 | 28520.64 | EA | 57041.28
22 | 9.504 | Earth work excavation of pits in hard rock requiring blasting.(wherever feasible/ required) | Elect | Labour | SWR20769 | 1012.35 | M3 | 9621.3744
23 | 2 | Erection of M+3 Tower (Galvanized) | Elect | Labour | SWR11850 | 64576 | EA | 129152
24 | 2 | Erection of Extension of 3Mtrs for M+3 (Galvanized) | Elect | Labour | SWR11851 | 5168.95 | EA | 10337.9
25 | 2 | Formation of Cut point for 33 KV Double circuit line excluding pole erection and stays | Elect | Labour | SWR10466 | 3198.72 | EA | 6397.44
26 | 4 | Supply of CI eath pipe with 80mm dia,2.75 M Length | Elect | Supply | SMR11483 | 2789 | EA | 11156
27 | 4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 4936.8
28 | 4 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 1544
29 | 2 | Dismantleing Rail pole 90 lbs | Elect | Labour | SWR11322 | 900 | EA | 1800
30 | 0.2 | Dismantling of 100 Sqmm Conductor DC Line. | Elect | Labour | SWR22064 | 11816.7 | KM | 2363.34
31 | 2 | Dismantling of M type tower | Elect | Labour | SWR11122 | 3484 | EA | 6968
32 | 2.802 | LOADING of MS Scrap | Elect | Labour | SWR10258 | 578 | TO | 1619.556
33 | 2.802 | UNLOADING of MS Scrap | Elect | Labour | SWR10576 | 578 | TO | 1619.556
34 | 0.181 | LOADING of ACSR conductor scrap | Elect | Labour | SWR10257 | 490.99 | TO | 88.8692
35 | 0.181 | UNLOADING of ACSR conductor scrap | Elect | Labour | SWR10575 | 490.99 | TO | 88.8692
36 | 2.983 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10148 | 481.44 | TO | 1436.1355
37 | 41.67 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 1708.47
38 | 0.15 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 513.9
39 | 4 | Dimantling of Extension of M+3 Tower | Elect | Labour | SWR12480 | 2584.48 | EA | 10337.92
40 | 14 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 14336
41 | 7 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excludingof loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 23097.9
42 | 14 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 14336
43 | 150 | Excavation & laying of UG Cable (Triple Run ) - Laying of 11 KV 3x300 Sqmm XLPE UG cable Triple Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 1050mm for 11 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - Along the CC / BT multi layer road requiring compressor - 11 KV 3x300 Sqmm Cable | Elect | Labour | SWR12020 | 1578.45 | M | 236767.5
44 | 250 | Excavation & laying of UG Cable (Double Run) - Laying of 11 KV 3x300 Sqmm Cable Double Run including excavation of trench of size 600mm and wide1050mm for 11 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc.. (Second cable laying cost not Included) depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs- Along the CC / BT multi layer road requiring compressor - 11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11981 | 1264.64 | M | 316160
45 | 350 | Excavation & laying of UG Cable in Single Run - Laying of 11KV 3x300sqmm XLPE UG cable Single Run including excavation of trench of size 450mm wide and 1050mm for 11KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs Providing of RFID markers on Shabad Stones wherever required, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc..depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - Along the CC / BT multi layer road requiring compressor-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11928 | 1073.94 | M | 375879
46 | 2500 | Laying of Second 33KV UG Cb in Existing Duct | Elect | Labour | SWR12452 | 200 | M | 500000
47 | 550 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 112255
48 | 14 | Making of 11 KV 3x300 Sqmm Cable Straight through joints | Elect | Labour | SWR10386 | 3725.45 | EA | 52156.3
49 | 650 | Supply 6" B Class GI pipe 5mm thck 20Kg/M | Elect | Supply | SMR40081 | 1344 | M | 873600
50 | 50 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 50600
51 | 8 | Making of 11 KV 3x300 Sqmm Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10391 | 2370.63 | EA | 18965.04
52 | 60 | Raising of Double run 11 KV 3x300 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR12005 | 275.4 | M | 16524
53 | 40 | Raising of Single run 11 KV 3x300 Sqmm Cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11955 | 144.08 | M | 5763.2
54 | 0.75 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 165.75
55 | 0.75 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 138.75
56 | 2 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 152
57 | 1.25 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 515.1
58 | 2 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 100
59 | 2 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 1025.1
60 | 2 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 2264
61 | 1 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 990.68
62 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 5568
63 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 2643.83
64 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - 9.1M PSCC Pole | Elect | Labour | SWR10343 | 2400 | EA | 14400
65 | 84 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 3444
66 | 5.32 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 35000.28
67 | 0.031 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3892.9 | M3 | 120.6799
68 | 0.75 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2569.5
69 | 5 | Supply of CI eath pipe with 80mm dia,2.75 M Length | Elect | Supply | SMR11483 | 2789 | EA | 13945
70 | 5 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 6171
71 | 5 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 1930
72 | 10 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 4840
73 | 1 | RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elect | Labour | SWR21843 | 25967.57 | EA | 25967.57
74 | 1 | Erection of Three Phase DTRs | Elect | Labour | SWR10463 | 1139.95 | EA | 1139.95
75 | 1 | Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10238 | 80 | EA | 80
76 | 1 | Un loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10556 | 80 | EA | 80
77 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR20102 | 1813.49 | EA | 1813.49
78 | 1 | Loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10231 | 18 | EA | 18
79 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
80 | 1 | Un loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10549 | 18 | EA | 18
81 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 740.52 | SET | 740.52
82 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elect | Labour | SWR10674 | 1594.67 | EA | 1594.67
83 | 0.3 | Stringing of LT AB cable 3x70 + 1x16 + 1x50 | Elect | Labour | SWR10666 | 8450 | KM | 2535
84 | 6 | Supply of Suspension Clamp Assembly & Eye Hook-M | Elect | Supply | SMR11492 | 65 | EA | 390
85 | 6 | Erection of Suspension Clamp Assemb &Eye hook-L | Elect | Labour | SWR12512 | 8 | EA | 48
86 | 2 | Supply of Dead End Clamp Assembly & Eye Hook-M | Elect | Supply | SMR11493 | 80 | EA | 160
87 | 2 | Erection of Dead End Clamp Assemb & Eye hook-L | Elect | Labour | SWR12513 | 8 | EA | 16
88 | 1 | Dismantle of 3-Ph DTR ( Upto 160 KVA) | Elect | Labour | SWR11729 | 975.12 | EA | 975.12
89 | 1 | Dismantle-3Ph 100KVA DTR Plinth | Elect | Labour | SWR12198 | 1160.25 | EA | 1160.25
90 | 1 | Dismantle of 11KV AB Switch TT Type | Elect | Labour | SWR12172 | 889.73 | EA | 889.73
91 | 5 | Dismantle of 9.1 M long PSCC pole | Elect | Labour | SWR11320 | 948.09 | EA | 4740.45
92 | 1 | Dismantle of Box pole 9/10/11 Mtr | Elect | Labour | SWR11329 | 1130 | EA | 1130
93 | 0.2 | Dismantling of 11kV 34/ 55 Sqmm SC Line | Elect | Labour | SWR22065 | 4500 | KM | 900
94 | 50 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 5875
95 | 1 | Dismantle of LT distribution box | Elect | Labour | SWR20075 | 669.38 | EA | 669.38
96 | 1 | Dimantle of 11KV HG Fuse Set incl earthing | Elect | Labour | SWR11745 | 353.43 | SET | 353.43
97 | 1 | LOADING of 11KV 5 Way RMU | Elect | Labour | SWR10616 | 1268.63 | EA | 1268.63
98 | 1 | UNLOADING of 11KV 5 Way RMU | Elect | Labour | SWR10630 | 1268.63 | EA | 1268.63
99 | 1 | Construction of plinth for mount. new 5Way RMU | Elect | Labour | SWR10731 | 8000 | EA | 8000
100 | 1 | Erection of 5-Way RMU | Elect | Labour | SWR11069 | 2783.33 | EA | 2783.33
101 | 2 | Supply of CI eath pipe with 50mm dia,2.0 M Length | Elect | Supply | SMR11484 | 2441 | EA | 4882
102 | 20 | Supply of GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 2100
103 | 33.33 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Elect | Labour | SWR12125 | 14.03 | M | 467.6199
104 | 2 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 2468.4
105 | 2 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 772
106 | 2 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 106
Total (Excl.GST) in Rs: | [7 empty] | 8061683.2601
GST @ 18 % | [7 empty] | 1451102.9868
Total (Incl. GST) in Rs: | [7 empty] | 9512786.2469
* The work will be taken up after completion of GHMC high level Bridge on Musi River at Moosarambagh ( The GHMC authorities provided Utility Duct on Bridge)