## F-2026-07-05-01-03-001
Schedule(WBS No:F-2026-07-05-01-03-001)
Name of the work :Extension of supply to 1-ph each 1KW 864 Nos Domestic services, 8 Nos each 16KW [Cat-I b(ii)] for common services, 64 Nos each 1 Kw (Cat-II) for shops, 4nos each 8 HP (Cat-VI-B) for bore motors, 1No. 6KW (Cat-VIA) for street lights thus making a total load of 1086KW at 2BHK houses in S+S+9 pattern for providing External Electrification arrangements to the 2 BHK housing colonies, at Sy No.453/5 & 453/6 in Dundigal (Vg) in Bachpally (M) of Quthbullapur Constituency of GHMC in Operation DP Pally Section, Shapurnagar Sub-Division in Jeedimetla Division of Medchal Circle under 2 BHK Scheme works
Sl.No. | SSR CODES | Estimate Quantity (Only figures) | Particulars | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item Short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR20102 | 8 | Erection of AB Switch and aligment complete.11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Erection work | Erection work | As per relevent standard specification | 1922.3 | EA | 15378.4
2 | SWR10343 | 36 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation.9.1 M long PSCC pole | Erection work | Erection work | As per relevent standard specification | 2400 | EA | 86400
3 | SWR10356 | 19.44 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Erection work | Erection work | As per relevent standard specification | 6579 | M3 | 127895.76
4 | SWR21844 | 8 | Construction of DTR Plinth.RCC Column type DTR Plinth of size 1'X1'X13',topslab 5'x9'x9" & beam size 5'X9'X9" above 160KVA | Erection work | Erection work | As per relevent standard specification | 27601 | EA | 220808
5 | SWR10357 | 24 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Earthing work | Earthing work | As per relevent standard specification | 1234.2 | EA | 29620.8
6 | SWR10395 | 8 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc.11 KV HG Fuse set including earthing | Erection work | Erection work | As per relevent standard specification | 740.52 | SET | 5924.16
7 | SWR10320 | 50 | Fabrication of materials including 2 coats of Red oxide painting.Back clamps with 50 x 6 mm MS Flat | Fabrication work | Fabricationwork | As per relevent standard specification | 16.5 | EA | 825
8 | SWR21590 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation.8.0 m long PSCC poles for Strut | Erection work | Erection work | As per relevent standard specification | 1500 | EA | 12000
9 | SWR10674 | 8 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Erection work | Erection work | As per relevent standard specification | 1690.35 | EA | 13522.8
10 | SMR11483 | 24 | Supply of earthing pipe with materials, CI eath pipe with 80mm dia,2.0 M Length | Earthing work | Earthing work | As per relevent standard specification | 2789 | EA | 66936
11 | SMR11488 | 300 | Supply of earthing pipe with materials,GI Bolts & Nuts etc | Earthing work | Earthing work | As per relevent standard specification | 117.5 | KG | 35250
12 | SWR10336 | 8 | Erection of CT operated meters for LV side of Distribution Transformers.Erection & ommissioning of CT meter along with box on LV side of DTRs including cable connections from Transformer LV to Distribution box via CT meters box | Erection work | Erection work | As per relevent standard specification | 900 | EA | 7200
13 | SWR10454 | 0.5 | Stringing of HT AB Cable with GI Metal Parts.HT AB Cable 11 KV 3x185+70 Sqmm | Stringing work | Stringing work | As per relevent standard specification | 41876.1 | KM | 20938.05
14 | SWR10672 | 30 | Straight through joints of AB cable (each lead).Supply and ere Straight line Asmbly kits | Erection work | Erection work | As per relevent standard specification | 1661 | EA | 49830
15 | SWR10673 | 16 | Straight through joints of AB cable (each lead) Supply and ere Angle line Asmbly kits | Erection work | Erection work | As per relevent standard specification | 2124 | EA | 33984
16 | SWR10667 | 12 | End Termination of AB cable (each lead):120 Sqmm to 185 Sqmm | Erection work | Erection work | As per relevent standard specification | 800 | EA | 9600
17 | SWR21850 | 3 | T Branch Kit.Erection of 11KV T - Branch kit | Erection work | Erection work | As per relevent standard specification | 200 | EA | 600
18 | SWR10105 | 8 | Excavation of pits in all soils except hard rock requiring blasting.8.0Mtrs PSCC Poles - 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x5.0') 0.88 cum | Excavation work | Excavation work | As per relevent standard specification | 650 | EA | 5200
19 | SMR11504 | 12 | End Termination of AB cable (each lead):Supply of 11KV 3x185+70sq.mm/ 3x70+70sq.mm/3x35+35sq.mm AB cable end Kits | Erection work | Erection work | As per relevent standard specification | 950 | SET | 11400
20 | SWR11037 | 36 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Excavation work | Excavation work | As per relevent standard specification | 793 | EA | 28548
21 | SMR11485 | 600 | Supply of earthing pipe with materials.GI Flat 25X3 mm | Earthing work | Earthing work | As per relevent standard specification | 105 | KG | 63000
22 | SWR10642 | 4 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Fabrication work | Fabricationwork | As per relevent standard specification | 512.55 | EA | 2050.2
23 | SWR11267 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation.Box pole 12 Mtr | Erection work | Erection work | As per relevent standard specification | 3901.37 | EA | 7802.74
24 | SWR10640 | 2 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Erection work | Erection work | As per relevent standard specification | 1132 | EA | 2264
25 | SWR21190 | 8 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits any and leveling the site with out any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Excavation work | Excavationwork | As per relevent standard specification | 520 | EA | 4160
26 | SWR10353 | 8 | Assembly and erection of stay set including fixing of guy insulators, clamps etc., on the pole and fixing stay wire and binding securely on either side as per standards,transport of material from road side to location and back filling with earth ramming 11 KV and LT | Erection work | Erection work | As per relevent standard specification | 606.85 | SET | 4854.8
27 | SWR10359 | 24 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Earthing work | Earthing work | As per relevent standard specification | 386 | EA | 9264
28 | SWR10313 | 38 | Fabrication of materials including 2 coats of Red oxide painting.1.07 mt. V. Cross arms with 75 x 40 mm MS Channel | Fabrication work | Fabricationwork | As per relevent standard specification | 116.37 | EA | 4422.06
29 | SWR10296 | 150 | Cutting charges for MS Sections.MS Angle of all sizes | Erection work | Erection work | As per relevent standard specification | 7 | EA | 1050
30 | SWR10134 | 2.4 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )Above 30 KM and upto 50 KM | Erection work | Erection work | As per relevent standard specification | 587.52 | TO | 1410.048
31 | SWR10204 | 4 | Loading of R.S. Joists 175 x 85 mm | LOADING | LOADING of work | As per relevent standard specification | 76 | EA | 304
32 | SWR10522 | 4 | Un loading of R.S. Joists 175 x 85 mm | UNLOADING | UNLOADING of work | As per relevent standard specification | 50 | EA | 200
33 | SWR10206 | 1.4 | Loading of M.S.Channels, Angles, Flats & Rods etc., | LOADING | LOADING of work | As per relevent standard specification | 221 | TO | 309.4
34 | SWR10524 | 1.4 | UNLoading of M.S.Channels, Angles, Flats & Rods etc., | UNLOADING | UNLOADING of work | As per relevent standard specification | 185 | TO | 259
35 | SWR10231 | 8 | Loading of 11 KV HG Fuse Sets | LOADING | LOADING of work | As per relevent standard specification | 18 | EA | 144
36 | SWR10549 | 8 | UNLoading of 11 KV HG Fuse Sets | UNLOADING | UNLOADING of work | As per relevent standard specification | 18 | EA | 144
37 | SWR11132 | 8 | Loading of LT Distribution Box | LOADING | LOADING of work | As per relevent standard specification | 18 | EA | 144
38 | SWR11133 | 8 | UNLoading of LT Distribution Box | UNLOADING | UNLOADING of work | As per relevent standard specification | 18 | EA | 144
39 | SWR10248 | 8 | Loading of Three Ph. LT Trivetor Meter with Box | LOADING | LOADING of work | As per relevent standard specification | 15 | EA | 120
40 | SWR10566 | 8 | UNLoading of Three Ph. LT Trivetor Meter with Box | UNLOADING | UNLOADING of work | As per relevent standard specification | 15 | EA | 120
41 | SMR12099 | 46 | Supply and Erection of I Hook and Suspension Hook.Supply of I hook | Erection work | Erection work | As per relevent standard specification | 158 | EA | 7268
42 | SWR12099 | 46 | Supply and Erection of I Hook and Suspension Hook.Erection of I hook | Erection work | Erection work | As per relevent standard specification | 55 | EA | 2530
43 | SWR25555 | 2000 | S&I-DTR Fence with Mesh200x100mm FRP Prf | Erection work | Erection work | As per relevent standard specification | 200.45 | FT2 | 400900
44 | SWR23098 | 8 | Fix-GPRS Modem & Sim Card | Erection work | Erection work | As per relevent standard specification | 300 | EA | 2400
45 | SWR10671 | 4 | Erection of Assemble Kit for 'T' Branche | Erection work | Erection work | As per relevent standard specification | 1800 | EA | 7200
46 | SWR24971 | 4 | Supply and erection of T-Branch kit | Erection work | Erection work | As per relevent standard specification | 3215 | EA | 12860
47 | SWR22356 | 500 | Laying/ Raising of LT UG cable, 1Core XLPE 120Sqmm Cable | Erection work | Erection work | As per relevent standard specification | 20 | M | 10000
48 | SWR11863 | 2.4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates. Above 30 Km and upto 50 Km with Lorry for each trip | Transport work | Transport work | As per relevent standard specification | 4372.74 | EA | 10494.576
49 | SWR12413 | 2 | Loading of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts. Drum (including Accessories ) | LOADING | LOADING of work | As per relevent standard specification | 584 | DR | 1168
50 | SWR12431 | 2 | Un loading of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts. Drum (including Accessories ) | UNLOADING | UNLOADING of work | As per relevent standard specification | 438 | DR | 876
51 | SWR12415 | 1 | Loading of LT Cable /AB Cable (XLPE) Single core Drum (including Accessories) for all size | LOADING | LOADING of work | As per relevent standard specification | 500 | DR | 500
52 | SWR12433 | 1 | Un loading of LT Cable /AB Cable (XLPE) Single core Drum (including Accessories) for all size | UNLOADING | UNLOADING of work | As per relevent standard specification | 260 | DR | 260
53 | SWR12406 | 8 | Loading of 11 KV AB SWCH T.T.200/400 A | LOADING | LOADING of work | As per relevent standard specification | 80 | EA | 640
54 | SWR12425 | 8 | UNLoading of 11 KV AB SWCH T.T.200/400 A | UNLOADING | UNLOADING of work | As per relevent standard specification | 80 | EA | 640
55 | SMR24769 | 40 | S-PVC Cleat 185sqmm | Suply | Supply of work | As per relevent standard specification | 38 | EA | 1520
56 | SWR20905 | 8 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc.3 Phase DTRs 63,75 & 100 KVA | Erection work | Erection work | As per relevent standard specification | 1815 | EA | 14520
57 | SWR10365 | 0.8 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location.55 Sqmm Single Circuit (3onductors) | stringing work | stringing work | As per relevent standard specification | 10400.29 | KM | 8320.232
58 | SWR10261 | 2.4 | Loading of Un winding of conductor including weighing per KM dog & rabbit | LOADING | LOADING of work | As per relevent standard specification | 237 | KM | 568.8
59 | SWR10579 | 2.4 | Un loading of Un winding of conductor including weighing per KM dog & rabbit | UNLOADING | UNLOADING of work | As per relevent standard specification | 237 | KM | 568.8
60 | SWR10196 | 8 | Loading of 160 & 250 KVA DTR | LOADING | LOADING of work | As per relevent standard specification | 468 | EA | 3744
61 | SWR10514 | 8 | UNLoading of 160 & 250 KVA DTR | UNLOADING | UNLOADING of work | As per relevent standard specification | 441 | EA | 3528
62 | SWR10765 | 16 | Making of Outdoor/Indoor End Termination.Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | Erection work | Erection work | As per relevent standard specification | 968.9 | EA | 15502.4
63 | SMR23100 | 928 | Supply and Erection of Metering Panel 14 G with all accessories.Supply & Erection of 1Ph metering panel (14 guage) with platform.Fixing of 1Ph meter, S & F of 1Ph MCB with including busbars, wiring and all accessories in complete shape - excluding of control panel | Erection work | Erection work | As per relevent standard specification | 2000 | EA | 1856000
64 | SMR11485 | 200 | Supply of earthing pipe with materials.GI Flat 25X3 mm. | Erthing work | Erthing work | As per relevent standard specification | 105 | KG | 21000
65 | SWR12009 | 200 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) LT 3 1/2 x 185 Sqmm Cable. | Erection work | Erection work | As per relevent standard specification | 160.65 | M | 32130
66 | SWR11977 | 1050 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet,3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts.In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC.LT 3 1/2 x 185 Sqmm Cable | Erection work | Erection work | As per relevent standard specification | 531.95 | M | 558547.5
67 | SMR23101 | 5 | Supply and Erection of Metering Panel 14 G with all accessories.Supply & Erection of 3Ph metering panel (14 guage) with platform. Fixing of 3Ph meter, S & F of 3Ph MCB with including busbars, wiring and with all accessories in complete shape - excluding of control panel | Erection work | Erection work | As per relevent standard specification | 3500 | EA | 17500
68 | SWR10342 | 38 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation.8.0 m long PSCC pole | Erection work | Erection work | As per relevent standard specification | 1500 | EA | 57000
69 | SWR10666 | 1080 | Stringing of LT AB Cable.LT AB cable 3x70 + 1x16 + 1x50 | Stringing work | Stringing work | As per relevent standard specification | 9295 | KM | 10038600
70 | SWR10356 | 16.42 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Erection work | Erection work | As per relevent standard specification | 6579 | M3 | 108027.18
71 | SWR11037 | 38 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Excavation work | Excavationwork | As per relevent standard specification | 793 | EA | 30134
72 | SWR21897 | 5 | Formation of Cut point for LT line excluding pole erection and stays for 3/4/5 wire | Erection work | Erection work | As per relevent standard specification | 938 | EA | 4690
73 | SWR10357 | 32 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Erection work | Erection work | As per relevent standard specification | 1234.2 | EA | 39494.4
74 | SMR40003 | 500 | Cost of Pipes and slabs. Suppy of Hume pipe 4" size | Erection work | Erection work | As per relevent standard specification | 80 | M | 40000
75 | SMR11609 | 100 | Cost of Pipes and slabs.supply of 4" DWC pipe | Erection work | Erection work | As per relevent standard specification | 759 | M | 75900
76 | SMR40140 | 16 | Making of Outdoor/Indoor End Termination.Supply of 31/2x185Sqmm UG O/D end termination kits | Erection work | Erection work | As per relevent standard specification | 550 | EA | 8800
77 | SWR10359 | 32 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Erthing work | Erthing work | As per relevent standard specification | 386 | EA | 12352
78 | SWR10244 | 10 | Loading of Single phase Meters -100nos lot | LOADING | LOADING of work | As per relevent standard specification | 128 | EA | 1280
79 | SWR10245 | 1 | Loading of Three Phase Meters -100nos lot | LOADING | LOADING of work | As per relevent standard specification | 240 | EA | 240
80 | SWR11232 | 2500 | Loading of 11KV/33 KV XLPE UG cable for all sizes | LOADING | LOADING of work | As per relevent standard specification | 18 | M | 45000
81 | SWR11233 | 2500 | Un loading of 11KV/33 KV XLPE UG cable for all sizes | UNLOADING | UNLOADING of work | As per relevent standard specification | 18 | M | 45000
82 | SWR10562 | 10 | Un loading of Single phase Meters -100nos lot | UNLOADING | UNLOADING of work | As per relevent standard specification | 128 | EA | 1280
83 | SWR10563 | 1 | Un loading of Three Phase Meters -100nos lot | UNLOADING | UNLOADING of work | As per relevent standard specification | 240 | EA | 240
84 | SWR24835 | 32 | Erection of Control panel. | Erection work | Erection work | As per relevent standard specification | 1800 | EA | 57600
85 | SMR24835 | 32 | Supply of Control Panel with busbars with required MCCBs including complete wiring | Erection work | Erection work | As per relevent standard specification | 18000 | EA | 576000
86 | SMR11594 | 60 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA.LED MAKE: PHILIPS UMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing,toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty.90W LED Fixture set | Erection work | Erection work | As per relevent standard specification | 8200 | EA | 492000
87 | SWR10956 | 60 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Erection work | Erection work | As per relevent standard specification | 1268 | EA | 76080
88 | SWR10988 | 1050 | Laying of 2nd cable in excavated trench | Erection work | Erection work | As per relevent standard specification | 204.1 | M | 214305
89 | SWR11863 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 30 Km and upto 50 Km with Lorry for each trip | Transport work | Transportwork | As per relevent standard specification | 4372.74 | EA | 4372.74
90 | SMR40091 | 32 | Earthing of Sub-Station.Supply of GI pipe 40 mm dia, 2 mtrs, 3mm thickness with bolts and nuts | Earthing work | Earthingwork | As per relevent standard specification | 733 | EA | 23456
91 | SWR10336 | 8 | Erection of CT operated meters for LV side of Distribution Transformers.Erection & commissioning of CT meter along with box on LV side of DTRs including cable connections from Transformer LV to Distribution box via CT meters box | Erection work | Erection work | As per relevent standard specification | 900 | EA | 7200
92 | SWR12433 | 2 | Un loading of LT Cable /AB Cable (XLPE) Single core Drum (including Accessories) for all size | UNLOADING | UNLOADING of work | As per relevent standard specification | 260 | DR | 520
93 | SWR12415 | 2 | Loading of LT Cable /AB Cable (XLPE) Single core Drum (including Accessories) for all size | LOADING | LOADING of work | As per relevent standard specification | 500 | DR | 1000
94 | SWR10320 | 52 | Fabrication of materials including 2 coats of Red oxide painting.Back clamps with 50 x 6 mm MS Flat | Fabrication | Fabrication of work | As per relevent standard specification | 16.5 | EA | 858
95 | SWR10223 | 8 | Loading of CT Metering boxes/ Distribution Boxes | LOADING | LOADING of work | As per relevent standard specification | 18 | EA | 144
96 | SWR10541 | 8 | Un loading of CT Metering boxes/ Distribution Boxes | UNLOADING | UNLOADING of work | As per relevent standard specification | 18 | EA | 144
97 | SWR11039 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders).9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Excavation work | Excavation work | As per relevent standard specification | 928 | EA | 1856
98 | SWR10356 | 2.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Erection work | Erection work | As per relevent standard specification | 6579 | M3 | 13815.9
99 | SWR10461 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc 11 KV VCB with Control Panel | Erection work | Erection work | As per relevent standard specification | 12000 | EA | 12000
100 | SMR11487 | 150 | Supply of earthing pipe with materials.MS bolts & nuts and washers etc of all sizes | Earthing work | Earthing work | As per relevent standard specification | 91.25 | KG | 13687.5
101 | SWR10393 | 4 | Erection of AB Switch and aligment complete.11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Erection work | Erection work | As per relevent standard specification | 3392 | EA | 13568
102 | SMR11482 | 3 | Supply of earthing pipe with materials.f CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Earthing work | Earthing work | As per relevent standard specification | 3486 | EA | 10458
103 | SWR10357 | 3 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Earthing work | Earthing work | As per relevent standard specification | 1234.2 | EA | 3702.6
104 | SWR10880 | 2 | Painting suppports of 0.3m with bitumen | Erection work | Erection work | As per relevent standard specification | 688 | EA | 1376
105 | SWR10640 | 2 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Erection work | Erection work | As per relevent standard specification | 1132 | EA | 2264
106 | SWR10881 | 2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete.(*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work.Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Erection work | Erection work | As per relevent standard specification | 142 | EA | 284
107 | SMR22473 | 3 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961)Supply of I Bolts | Erection work | Erection work | As per relevent standard specification | 294 | EA | 882
108 | SWR10423 | 3 | Fixing of clamps.I - bolts | Erection work | Erection work | As per relevent standard specification | 20 | EA | 60
109 | SWR10920 | 45 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.75x 8mm MS Flat / GI Flat. | Earthing work | Earthing work | As per relevent standard specification | 65 | RMT | 2925
110 | SWR10918 | 60 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 75x8mm / 75 x 12 mm | Fabrication work | Fabricationwork | As per relevent standard specification | 50 | RMT | 3000
111 | SWR10942 | 1 | Testing of Sub-Station Equipment.Wirring, commissioning and testing of Outdoor Sub-station switchgear duly conducting the pre commissioning test as per relevent standards & issue of certificate by CEIG authorised testing Engineer | Erection work | Erection work | As per relevent standard specification | 1825 | EA | 1825
112 | SWR20736 | 1 | Supply & fixing of 220 V DC Electronic Bell | Supply work | Supplywork | As per relevent standard specification | 400 | EA | 400
113 | SMR11485 | 40 | Supply of earthing pipe with materials.GI Flat 25X3 mm | Earthing work | Earthing work | As per relevent standard specification | 105 | KG | 4200
114 | SWR10856 | 3 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) (other than SS)Earth work excavtion hard rock boulders | Excavation work | Excavation work | As per relevent standard specification | 1318.35 | M3 | 3955.05
115 | SWR10398 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc.11 KV LAS line type including earthing | Erection work | Erection work | As per relevent standard specification | 505 | SET | 505
116 | SWR10404 | 50 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | Stringing work | Stringingwork | As per relevent standard specification | 327.68 | M | 16384
117 | SWR10642 | 2 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Fabrication work | Fabricationwork | As per relevent standard specification | 512.55 | EA | 1025.1
118 | SWR10134 | 2.6 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )Above 30 KM and upto 50 KM | Transport work | Transport work | As per relevent standard specification | 587.52 | TO | 1527.552
119 | SWR10199 | 1 | Loading of 11 KV VCBs along with Panel boards | LOADING | LOADING of work | As per relevent standard specification | 1024 | EA | 1024
120 | SWR10517 | 1 | Un loading of 11 KV VCBs along with Panel boards | UNLOADING | UNLOADING of work | As per relevent standard specification | 1044.48 | EA | 1044.48
121 | SWR10205 | 2 | Loading of R.S. Joists 150 x 150mm / Rail poles | LOADING | LOADING of work | As per relevent standard specification | 176 | EA | 352
122 | SWR10523 | 2 | UNLoading of R.S. Joists 150 x 150mm / Rail poles | UNLOADING | UNLOADING of work | As per relevent standard specification | 107 | EA | 214
123 | SWR10238 | 4 | Loading of 11KV AB Switch Conventional type | LOADING | LOADING of work | As per relevent standard specification | 80 | EA | 320
124 | SWR10556 | 4 | UNLoading of 11KV AB Switch Conventional type | UNLOADING | UNLOADING of work | As per relevent standard specification | 80 | EA | 320
125 | SWR10206 | 1.8 | Loading of M.S.Channels, Angles, Flats & Rods etc., | LOADING | LOADING of work | As per relevent standard specification | 221 | TO | 397.8
126 | SWR10524 | 1.8 | UNLoading of M.S.Channels, Angles, Flats & Rods etc., | UNLOADING | UNLOADING of work | As per relevent standard specification | 185 | TO | 333
127 | SWR10265 | 3 | Loading of 11 KV, 10 KA LAs Line type | LOADING | LOADING of work | As per relevent standard specification | 32 | EA | 96
128 | SWR10583 | 3 | UNLoading of 11 KV, 10 KA LAs Line type | UNLOADING | UNLOADING of work | As per relevent standard specification | 32 | EA | 96
129 | SWR11701 | 450 | Loading of PVC Control Cable 10 Core | LOADING | LOADING of work | As per relevent standard specification | 1 | M | 450
130 | SWR11712 | 450 | UNLoading of PVC Control Cable 10 Core | UNLOADING | UNLOADING of work | As per relevent standard specification | 1.02 | M | 459
131 | SWR12507 | 3 | Providing push button type LED lamps | Erection work | Erection work | As per relevent standard specification | 150 | EA | 450
132 | SWR11928 | 160 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable,placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.Along the CC / BT multi layer road requiring compressor.11 KV 3x300 Sqmm Cable | Excavation work | Excavation work | As per relevent standard specification | 1073.94 | M | 171830.4
133 | SWR11955 | 40 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) 11 KV 3x300 Sqmm Cable | Erection work | Erection work | As per relevent standard specification | 144.08 | M | 5763.2
134 | SWR10391 | 2 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Erection work | Erection work | As per relevent standard specification | 2370.63 | EA | 4741.26
135 | SWR11230 | 200 | Loading of 11KV/33KV XLPE UG Cable for all sizes | LOADING | LOADING of work | As per relevent standard specification | 1024 | DR | 204800
136 | SWR11231 | 200 | UNLoading of 11KV/33KV XLPE UG Cable for all sizes | UNLOADING | UNLOADING of work | As per relevent standard specification | 1024 | DR | 204800
137 | SWR10386 | 2 | UG Cables Joints : Making of Straight through joints.11 KV 3x300 Sqmm Cable | Erection work | Erection work | As per relevent standard specification | 3725.45 | EA | 7450.9
138 | SWR11172 | 2 | Loading of 33/KV XLPE UG CableStraight Through Joint Kits for all sizes | LOADING | LOADING of work | As per relevent standard specification | 8 | EA | 16
139 | SWR11153 | 2 | Un loading of 33/KV XLPE UG CableStraight Through Joint Kits for all sizes | UNLOADING | UNLOADING of work | As per relevent standard specification | 4 | EA | 8
140 | SWR10732 | 1 | Con of Plinth for 11kv VCB 1.8x1.8x0.75m | Erection work | Erection work | As per relevent standard specification | 27629 | EA | 27629
141 | SMR40009 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete.Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Erection work | Erection work | As per relevent standard specification | 2181 | TO | 3925.8
142 | SWR10877 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete.Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Erection work | Erection work | As per relevent standard specification | 851 | TO | 1531.8
143 | SMR40010 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete..*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Erection work | Erection work | As per relevent standard specification | 1293 | TO | 2327.4
144 | SWR10879 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete..(*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Erection work | Erection work | As per relevent standard specification | 482 | TO | 867.6
145 | SWR10869 | 1.8 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Fabrication work | Fabrication work | As per relevent standard specification | 3426 | TO | 6166.8
146 | SWR10348 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. R.S. Joists 150 x 150 mm | Erection work | Erection work | As per relevent standard specification | 1952.61 | EA | 3905.22
147 | SWR12294 | 3 | Excavatin of pit."Providing of Base Concreting with 1:3:6 Concrete Mix including materials & curing with water | Excavation work | Excavation work | As per relevent standard specification | 5053 | M3 | 15159
148 | SWR11879 | 450 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Excavation work | Excavation work | As per relevent standard specification | 27 | M | 12150
149 | SWR10869 | 2.2 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Fabrication work | Fabrication work | As per relevent standard specification | 3426 | TO | 7537.2
150 | SMR11915 | 6 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Supply work | Supply work | As per relevent standard specification | 2055 | SET | 12330
151 | SMR40011 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961)Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . | Supply work | Supply work | As per relevent standard specification | 299 | EA | 3588
152 | SWR12510 | 100 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Supply work | Supply work | As per relevent standard specification | 27 | EA | 2700
153 | SWR12331 | 4 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Supply work | Supply work | As per relevent standard specification | 146.63 | EA | 586.52
154 | SWR11863 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates.Above 30 Km and upto 50 Km with Lorry for each trip. | Transport work | Transport work | As per relevent standard specification | 4372.74 | EA | 4372.74
155 | SWR10205 | 2 | Loading of R.S. Joists 150 x 150mm / Rail poles | LOADING | LOADING of work | As per relevent standard specification | 176 | EA | 352
156 | SWR10523 | 2 | UNLoading of R.S. Joists 150 x 150mm / Rail poles | UNLOADING | UNLOADING of work | As per relevent standard specification | 107 | EA | 214
157 | SWR10917 | 24 | Labour for Fixing of all types of clamps | Erection work | Erection work | As per relevent standard specification | 65 | EA | 1560
158 | SMR40080 | 24 | Cost of Pipes and slabs.Supply of 4" B class GI pipe | Erection work | Erection work | As per relevent standard specification | 800 | M | 19200
159 | SWR33057 | 5 | S&Spreading of 20mm HBG Metal | Erection work | Erection work | As per relevent standard specification | 2041 | M3 | 10205
160 | SMR11594 | 1 | S-90W LED fixture set | Civil Work | Civil Work | As per relevent standard specification | 8200 | EA | 8200
161 | SWR10956 | 1 | Fixing of LED/Metal halide complete. | Civil Work | Civil Work | As per relevent standard specification | 1268 | EA | 1268
162 | SWR34179 | 8 | Hire-JCB to Level & Clear the Site | Civil Work | Civil Work | As per relevent standard specification | 2226.5 | H | 17812
163 | SWR33015 | 15.75 | Excavation in Ordinary Soil | Civil Work | Civil Work | As per relevent standard specification | 539.54 | M3 | 8497.755
164 | SWR33403 | 22.4 | S&F MS Security Fencing Mesh (2"X2") | Civil Work | Civil Work | As per relevent standard specification | 2192 | M2 | 49100.8
165 | SWR34470 | 3.63 | Seigniorage Charges - Sand | Civil Work | Civil Work | As per relevent standard specification | 40 | M3 | 145.2
166 | SWR34928 | 3.63 | Seigniorage Charges for M-Sand | Civil Work | Civil Work | As per relevent standard specification | 97.5 | M3 | 353.925
167 | SWR34471 | 24.97 | Seigniorage Charges - Metal | Civil Work | Civil Work | As per relevent standard specification | 30 | M3 | 749.1
168 | SWR34472 | 50 | Seigniorage Charges - Gravel | Civil Work | Civil Work | As per relevent standard specification | 75 | M3 | 3750
169 | SWR33041 | 22.7 | CRS Masonary CM(1:6) 2nd Sort | Civil Work | Civil Work | As per relevent standard specification | 5829 | M3 | 132318.3
170 | SWR33052 | 80 | S&Filling with Borrowed Gravel | Civil Work | Civil Work | As per relevent standard specification | 715 | M3 | 57200
171 | SWR33028 | 2.5 | PCC with 40mm Metal (1:4:8) | Civil Work | Civil Work | As per relevent standard specification | 5556 | M3 | 13890
172 | SWR33030 | 0.8 | PCC with 20mm Metal (1:2:4) | Civil Work | Civil Work | As per relevent standard specification | 6967 | M3 | 5573.6
|  |  |  | Schedule Cost. (Excluding GST) |  |  |  |  | 16986764.348
|  |  |  | GST@18% |  |  |  |  | 3057617.5826
|  |  |  | Schedule Cost Total |  |  |  |  | 20044381.9306