## Sheet6 (hidden)
Row Labels | Sum of quantity | Sum of Price
SFU10032 | 39 | 49701.6
SFU10042 | 29 | 49561.29
STR10233 | 197 | 49978.9
TS100054 | 219 | 149062.32
Grand Total | 484 | 298304.11

## Sheet5 (hidden)
mat code | mat desc | quantity | Price
SFU10032 | T.C.Fuse Wire 12swg (50swg) | 39 | 49701.6
TS100054 | Rubber Hand Glovses-Pair | 81 | 49892.76
SFU10042 | T.C.Fuse Wire 33swg | 29 | 49561.29
STR10233 | LV Brass Bush rods 180X12mm(1/2"x7") | 197 | 49978.9
TS100054 | Rubber Hand Glovses-Pair | 69 | 49584.78
TS100054 | Rubber Hand Glovses-Pair | 69 | 49584.78

## Sheet4 (hidden)
Row Labels | Sum of QUANTITY | Sum of TOTAL
SAB10001 | 381 | 193319.4
SAB10002 | 602 | 305454.8
SAB10008 | 360 | 360000
SAB10009 | 184 | 351440
SFU10032 | 200 | 318600
SFU10042 | 55 | 93456
SSB10027 | 220 | 114224
SSB10098 | 500 | 240000
TS100054 | 321 | 215668.02
Grand Total | 2823 | 2192162.22

## Sheet2 (hidden)
MAT CODE | MAT DESC | QUANTITY | UNIT PRIICE | TOTAL
SAB10001 | 11KV 200A TT AB switch fixed contacts | 381 | 507.4 | 193319.4
SAB10002 | 11KV 200A TT AB switch moving contacts | 602 | 507.4 | 305454.8
SAB10008 | 11KV 400A Conv. AB switch fixed contacts | 180 | 1000 | 180000
SAB10008 | 11KV 400A Conv. AB switch fixed contacts | 180 | 1000 | 180000
SAB10009 | 11KV 400A Conv. AB switch moving contact | 92 | 1910 | 175720
SAB10009 | 11KV 400A Conv. AB switch moving contact | 92 | 1910 | 175720
SFU10032 | T.C.Fuse Wire 12swg (50swg) | 100 | 1593 | 159300
SFU10032 | T.C.Fuse Wire 12swg (50swg) | 100 | 1593 | 159300
SFU10042 | T.C.Fuse Wire 33swg | 55 | 1699.2 | 93456
SSB10027 | T Clamp for Panther to Panther Cd-12bolt | 110 | 519.2 | 57112
SSB10027 | T Clamp for Panther to Panther Cd-12bolt | 110 | 519.2 | 57112
SSB10098 | 4 Hole 6 Bolted Pad Clamp for Panther Cd | 250 | 480 | 120000
SSB10098 | 4 Hole 6 Bolted Pad Clamp for Panther Cd | 250 | 480 | 120000
TS100054 | Rubber Hand Glovses-Pair | 58 | 659.32 | 38240.56
TS100054 | Rubber Hand Glovses-Pair | 80 | 574 | 45920
TS100054 | Rubber Hand Glovses-Pair | 60 | 718.62 | 43117.2
TS100054 | Rubber Hand Glovses-Pair | 60 | 718.62 | 43117.2
TS100054 | Rubber Hand Glovses-Pair | 63 | 718.62 | 45273.06

## paper notification (2)
TENDER NOTIFICATION NO.02/2024-2025
LIST OF MATERIALS FOR PROCUREMENT OF O & M MATERIAL THROUGH OPEN TENDER
S.No | Specification No | Material code | MAT NAME | MAT DESCRIPTION | SAP PLAN PRICE | Quantity | Approx Cost in Rs | EMD in Rs | Bid Cost in Rs | Bid issueStart Date | Bid issue End Date & time | Last Date & time for Submission of Bid | Bid opening date & time | Tender to be processed at
1 | P-1 | SAB10001 | 11KV 200A TT AB switch fixed contacts | Fixed contact Assembly: Fixed contact suitable for 11kv 200.A (Tilting type)AB Switches shall be of high grade copper and capable of Carrying the short circuit current of 16 KA (min) and capable of carrying, rated normal current of the switch continuously the contact shall be 30 X 6 X 225 mm copper flat nickel plated and with 14 SWG gauge phosphor bronze arcing horn suitable for the above switch. | 428.99 | 699.317 | 300000 | 7080 | 590 | 01.08.2024 | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs | SE/OP/RAJENDRANAGAR
2 | P-2 | SAB10002 | 11KV 200A TT AB switch moving contacts | Moving contact for 11 KV 200A (16KA load break) Tilting type AB switch consisting of jaw cup of 220 x 70 x 2 mm with jumper pad of HDEC 30 x 6 125 mm with and arcing horn of 5 mm dia St. steel rod to fix in jaw cup with studs and nuts and with St.steel springs (2 Nos.) | 457.04 | 656.3977 | 300000 | 7080 | 590 | 01.08.2024 | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs | SE/OP/RAJENDRANAGAR
3 | P-3 | SAB10004 | 11KV 200A Conv. AB switch fixed contacts | Consisting of 2 Nos. self released jaws type fixed contact 25 x 4 x 100 mm copper strip Tin plated suitable for 11 KV 200 A/400A (Cony.) AB Switches duly butting to the jumper pad with 10 Nos. Cu strips for each jaw (the contacts designed to carry current the temp. rise does not increase beyond the value specified in IS i.e. 40 degree C above ambient) and 2 sets of St.Steel (Non-magnetic springs each provided on either side of fixed contact blades so that smooth contact is made for making and breaking contact and MSHDG top and bottom housing arcing horn of 6 mm dia MSHDG with required bolts and nuts. | 1029.66 | 291.3583 | 300000 | 7080 | 590 | 01.08.2024 | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs | SE/OP/RAJENDRANAGAR
4 | P-4 | SAB10005 | 11KV 200A Conv. AB switch moving contact | Moving contact HDEC (nife) electroplated with Swivelling plate (HDEC), Arcing horn 6 mm dia MSHDG and copper flexible jumper (1 no. for 200 Amps AB Switch) with required bolts and nuts.Nife size 32x5x320 mm, Swivelling plate size plate size 32x5x145 mm and one no. flexible jumper of size 25x4x360 mm | 2183 | 137.4256 | 300000 | 7080 | 590 | 01.08.2024 | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs | SE/OP/RAJENDRANAGAR
5 | P-5 | SAB10008 | 11KV 400A Conv. AB switch fixed contacts | Consisting of 2 Nos. self released jaws type fixed contact 25 x 4 x 100 mm copper strip Tin plated suitable for 11 KV 200 A/400A (Cony.) AB Switches duly butting to the jumper pad with 10 Nos. Cu strips for each jaw (the contacts designed to carry current the temp rise does not increase beyond the value specified in IS i.e. 40 degree C above ambient) and 2 sets of St.Steel (Non-magnetic springs each provided on either side of fixed contact blades so that smooth contact is made for making and breaking contact and MSHDG top and bottom housing arcing horn of 6 mm dia MSHDG with required bolts and nuts. | 999.14 | 300.2582 | 300000 | 7080 | 590 | 01.08.2024 | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs | SE/OP/RAJENDRANAGAR
6 | P-6 | SAB10009 | 11KV 400A Conv. AB switch moving contact | Moving contact HDEC (nife) electroplated with Swivelling plate (HDEC), Arcing horn 6 mm dia MSHDG and copper flexible jumper (1 no. for200 Amps AB Switch) with required bolts and nuts.Nife size 32x6x320 mm, Swivelling plate size plate size 32x6x145 mm and one no. flexible jumper of size 25x4x360 mm | 1680.16 | 178 | 300000 | 7080 | 590 | 01.08.2024 | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs | SE/OP/RAJENDRANAGAR
7 | P-7 | SAB10033 | 11KV 400A DB AB Switch Moving Contact | 11kV 400 a double break moving contact for conventional AB switch of size 32 x 6 x810 mm HDEC Flat. | 2541.67 | 118.0326 | 300000 | 7080 | 590 | 01.08.2024 | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs | SE/OP/RAJENDRANAGAR
8 | P-8 | SFU10032 | T.C.Fuse Wire 12swg (50swg) | Annealed tinned copper fuse wire of pure electrolytic quality smoothly drawn approximately circular section and uniform as per IS 9926/1981 of latest edition 12 SWG in reels packing net weight should be l Kg without packing material | 1349.92 | 222.2354 | 300000 | 7080 | 590 | 01.08.2024 | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs | SE/OP/RAJENDRANAGAR
9 | P-9 | STR10233 | LV Brass Bush rods 180X12mm(1/2"x7") | LV Brass Bush rods Conventional type 180X12 mm with 4 nuts, not less than 180g weight. | 244.66 | 817.461 | 200000 | 4720 | 590 | 01.08.2024 | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs | SE/OP/RAJENDRANAGAR
10 | P-10 | SFU10035 | T.C.Fuse Wire 18swg for PTR | Annealed tinned copper fuse wire of pure electrolytic quality smoothly drawn approximately circular section and uniform as per IS 9926/1981 of latest edition 18SWG in reels packing net weight should be l Kg without packing material | 1692.24 | 88.6399 | 300000 | 7080 | 590 | 01.08.2024 | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs | SE/OP/RAJENDRANAGAR
11 |  | SFU10034 | T.C.Fuse Wire 16swg for PTR | Annealed tinned copper fuse wire of pure electrolytic quality smoothly drawn approximately circular section and uniform as per IS 9926/1981 of latest edition 16 SWG in reels packing net weight should be l Kg without packing material | 1618 | 92.707 |  |  |  |  | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs
12 | P-11 | SFU10042 | T.C.Fuse Wire 33swg | Annealed tinned copper fuse wire of pure electrolytic quality smoothly drawn approximately circular section and uniform as per IS 9926/1981 of latest edition 33SWG in reels packing net weight should be l Kg without packing material | 1709.82 | 116 | 200000 | 4720 | 590 | 01.08.2024 | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs | SE/OP/RAJENDRANAGAR
13 | P-12 | SSB10027 | T Clamp for Panther to Panther Cd-12bolt | Alluminum alloy T clamp minimum 150 x 70 x 15 mm, minimum weight of 1300 gms to suit for panther ACSR on all three ways for carrying 600 A current. Clamp contact surface should be smooth finished and maintain conforming to IS: 617 (latest edition), IS:5561-1970. | 489.02 | 613.4718 | 300000 | 7080 | 590 | 01.08.2024 | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs | SE/OP/RAJENDRANAGAR
14 | P-13 | SSB10098 | 4 Hole 6 Bolted Pad Clamp for Panther Cd | Four hole Six bolted Alluminum alloy Pad clamp 170 x 80 x 15 mm, with minimum weight of 900 gms to suit for Panther ACSR Conductor for carrying 600 A current. Clamp contact surface should be smooth finished and maintain conforming to IS: 617 (latest edition), IS:5561-1970. | 487 | 616.0164 | 300000 | 7080 | 590 | 01.08.2024 | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs | SE/OP/RAJENDRANAGAR
15 | P-14 | TS100054 | Rubber Hand Glovses-Pair | Seamless Rubber hand gloves with ISI Specifaction No. 4770 1968-1991 latest version with tested potential not less than 11000 V and working potential not less than 11000 V and working potential 1100 V of size of 355 mm length rubber hand gloves pair(right and left) of ISI Standard quality (as per approved sample) | 825.17 | 181 | 150000 | 3540 | 590 | 01.08.2024 | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs | SE/OP/RAJENDRANAGAR
16 | P-15 | TS100089 | Rain Coat with Cap (< Rs.1000/-) | Raincoats of Duckback Company/ Superior Quality consists of long coats with pouch and cap with TGSPDCL lettering, packed in a bag. | 900.16 | 300 | 250000 | 5900 | 590 | 01.08.2024 | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs | SE/OP/RAJENDRANAGAR
17 | P-16 | SLA10113 | 90W LED Yard Light-105-295V>120Lm/W | LED YARD Lights 90 W with fixuters of CGL/Baja make with ISI standards along with GI pipe and supported Clamps | 7952 | 80 | 300000 | 7080 | 590 | 01.08.2024 | 08.08.2024 | 09.08.2024 15:00 Hrs | 12.08.2024 11:00 Hrs | SE/OP/RAJENDRANAGAR
Sales from 01.08.2024 to 08.08.2024 and last date of submission is 09.08.2024 up to 15:00 hrs and Opening on 12.08.2024 at 11:00 hrs)
Copy to : Chief Engineer/IT/TGSPDCL